GUIDELINES FOR VULNERABILITY REDUCTION 
IN THE DESIGN OF NEW HEALTH FACILITIES

Rubén Boroschek Krauskopf, Ph.D.

Rodrigo Retamales Saavedra

PAHO/WHO Collaborating Center

Disaster Mitigation in Health Facilities

University of Chile

Pan American Health Organization

World Bank

ProVention Consortium

February 2003

Preface

Nowadays, when severe natural phenomena occur, health facilities generally experience temporary or permanent interruption of their services, damage to their infrastructure, and the partial or total loss of the considerable investment made in building and furnishing them—all of which has a significant negative impact on the social and economic development of the country and its inhabitants. Such situations arise because all too often, in the design of such facilities, the sole objective regarding the performance of the building in disaster situations has been protecting the lives of the staff and users. While this is an indispensable goal, and one that has been met with a certain degree of success, the consequence of such a limited vision has been, in practice, the building of facilities that offer little or no protection to the investment made or to their crucial function within the health system.

Historically, to make matters worse, the choice of where the facilities were to be located has often been made with little awareness of the natural hazards present in the area and their likely effects on structures, operations, and the surrounding community. Finally, it is by no means rare to find construction or maintenance practices that curtail or even neutralize altogether the few safety measures that were incorporated in the design of the facility.

A turnaround is needed.  While improving the safety of existing infrastructure is difficult and relatively costly, the incorporation of investment and functional protection in the design and construction of new facilities is simple and comparatively inexpensive. The value of applying such criteria has already been proven in such disasters as the earthquakes that hit Northridge (Los Angeles) in the United States in 1994 and Kobe in Japan in 1995, where hospitals and other important facilities within the epicenter area managed to remain in operation.

Such an approach, however, requires an awareness of the facility’s desirable level of performance in the face of different disaster scenarios of varying intensity. The objective can be life safety, investment protection, or functional protection. To reach the chosen objective it is necessary to reorganize the way in which new health facilities have traditionally been conceived and buil. What is needed is the use of designs and construction methods that take into account the natural hazards likely to affect the site and the surrounding region, as well as the performance objective desired. International experience shows that basing a new project on such a philosophy only increases total costs by less than 4 percent. This is a fraction of the direct losses the sector suffers annually as a result of insufficient disaster preparedness—not to mention the social, political, and economic impact of the breakdown in services, or the total loss of a costly and much needed hospital, laboratory, or blood bank, in the midst of a major emergency.

This handbook is aimed at health sector administrators, professionals, and consultants whose task is the management, design, construction, and inspection of new health facilities. It specifies the activities that must be carried out throughout all relevant stages, including preliminary planning, the selection of the team of professionals that will participate in the project, the choice of site, and the design and construction of the project itself.

PAHO/WHO Collaborating Center for

Disaster Mitigation in Health facilities

University of Chile

Chapter I

Natural Phenomena and Health Infrastructure

- Introduction

Major natural disasters in the last two decades have affected at least 800 million people.  They have caused thousands of deaths, as well as economic losses of more than 50 billion U.S. dollars. Growing population density in several regions of the planet—and the consequent settlement of high-risk areas—are likely to make matters worse. Between 1981 and 2001, according to the Pan American Health Organization, more than 100 hospitals and 650 health units in the hemisphere were severely damaged by the action of natural phenomena, causing direct economic losses of close to 3.1 billion dollars.

Tables 1 through 3 show some of the effects of adverse natural phenomena on health infrastructure.

| Table 1 Effects of Hurricanes On Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Nature of the Phenomenon | Overall Effects |
| Jamaica, Hurricane Gilbert | 1988 | Category 5 | 24 hospitals and health centers damaged or destroyed. 5,085 patient beds lost. |
| Costa Rica and Nicaragua, Hurricane Joan | 1988 | Category 4 | 4 hospitals and health centers damaged or destroyed. |
| Dominican Republic, Hurricane Georges | 1998 | Category 3 | 87 hospitals and health centers damaged or destroyed. |
| Saint Kitts-Nevis, Hurricane Georges | 1998 | Category 3 | Joseph N. France Hospital in Saint Kitts suffered severe damage. 170 beds lost. |
| Honduras, Hurricane Mitch | 1998 | Category 5 | 78 hospitals and health centers damaged or destroyed. Honduras’ national health network severely affected, rendered inoperative just as over 100,000 people needed urgent medical attention. |
| Nicaragua, Hurricane Mitch | 1998 | Category 5 | 108 hospitals and health centers damaged or destroyed. |

| Sources | : | Based on Natural Disasters: Protecting the Public Health, Scientific Publication Nº575, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |

| Table 2 Effects of Floods on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Nature of the Phenomenon | Overall Effects |
| Pacific and Andean Region of South America | 1997-1998 | Floods associated with the El Niño Phenomenon | The floods placed grueling demands on the health system to combat acute respiratory infections, acute diarrheic diseases, vector-borne diseases (malaria, classic dengue, hemorrhagic dengue, yellow fever, encephalitis, Chagas disease, etc.), water- and food borne diseases (cholera, salmonellosis, typhoid fever, viral hepatitis, multiple intestinal parasitism, etc.) and skin diseases (scabies, bacterial infections and mycoses, etc.). |
| Ecuador | 1997 | Floods associated with the El Niño Phenomenon | Chone Hospital, not yet inaugurated at the time of the flood, suffered severe losses in medical equipment, furnishings, supplies and drugs. |
| Venezuela | 1999 | Torrential rains affecting states along the Eastern, Central and Western coasts of the country | The floods affected 31 hospitals and 687 outpatient clinics. |

| Sources | : | Crónicas de Desastres Nº 8: Fenómeno El Niño 1997-1998, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |

| Table 3 Effects of Earthquakes on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Magnitude | Overall Effects |
| San Fernando, California | 1971 | 6.4 | Three hospitals suffered severe damage and were unable to operate normally at the very moment they were most needed. Worse still, most of the disaster-related deaths and injuries occurred in the two hospitals that collapsed. Olive View Hospital, one of the most severely affected, had to be demolished and rebuilt. Since this was done in the traditional fashion, however, the new facilities suffered severe non-structural damage in the earthquake of 1994, putting them out of service. |
| Managua, Nicaragua | 1972 | 5.6 | The General Hospital was severely damaged. It had to be evacuated and, subsequently, demolished. |
| Guatemala City, Guatemala | 1976 | 7.5 | Several hospitals required evacuation. |
| Popayán, Colombia | 1983 | 5.5 | Damage and interruption of services at the San José University Hospital. |
| Chile | 1985 | 7.8 | 79 hospitals and health centers damaged or destroyed. 3,271 beds lost. |
| Mendoza, Argentina | 1985 | 6.2 | Over 10 percent of the total hospital beds in the city were lost. Of the 10 facilities affected, one had to be evacuated; two were subsequently demolished. |

| Table 3 (Continued) Effects of Earthquakes on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Identity Event | Date | Magnitude | Overall effects |
| Mexico City, Mexico | 1985 | 8.1 | Structural collapse of five hospital facilities and major damage to another 22. At least 11 facilities had to be evacuated. Direct losses were estimated at US$ 640 million. The hospitals that suffered the most were the National Medical Center of the Mexican Social Security Institute (IMSS), the General Hospital, and Benito Juárez Hospital. Between the patient beds destroyed and those taken out of service due to evacuation, the seismic event caused a sudden deficit of 5,829 beds. At the General Hospital, 295 died; at the Juárez, 561. Among the casualties: patients, doctors, nurses, administrative staff, visitors, and newborns. |
| San Salvador, El Salvador | 1986 | 5.4 | 2,000 beds lost. Over 11 hospital facilities affected: 10 had to be evacuated, one condemned. Total damage was estimated at US$ 97 million. |
| Tena, Ecuador | 1995 | 6.2 | Velasco Ibarra Hospital (120 beds) suffered moderate non-structural damage—cracking on several walls, breaking of glass windows, collapse of ceilings, elevator system failure, and damage to water and oxygen pipes—forcing evacuation of the facilities. |
| Aiquile, Bolivia | 1998 | 6.8 | Carmen López Hospital severely damaged. |
| Armenia, Colombia | 1999 | 5.8 | 61 health facilities damaged. |
| El Salvador | 2001 | 7.6 | 1,917 hospital beds--39.1 percent of the country’s total capacity--lost. Severely damaged San Rafael Hospital was able to continue providing partial services—outdoors, on the hospital grounds. Rosales Hospital lost its capacity to provide surgical services as a result of the damage to several key wings. San Juan of Dios (San Miguel) and San Pedro (Usulután) Hospitals suffered considerable damage, and were only able to continue providing partial services outdoors, on their grounds. The Oncology Hospital had to be completely evacuated. |

| Sources | : | Based on Principles for Natural Disaster Mitigation in Health Facilities, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Based on Natural Disasters: Protecting the Public Health, Scientific Publication Nº575, Pan American Health Organization, 2000. |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |
|  |  | Daños Observados en los Hospitales de la Red de Salud Asistencial de El Salvador en el terremoto del 13 de Enero de 2001, Informe Preliminar, Boroschek, K. y R. Retamales, 2001. |

Adverse natural phenomena affect health systems’ operations in two ways:

- Directly, by

  - Damaging healthcare facilities.

  - Damaging the infrastructure of the region, leading to the breakdown of public services indispensable to health facility operations as well as the destruction of access roads.

- Indirectly, by

  - Causing an unexpected number of deaths, injuries, or disease outbreaks in the affected community, exceeding the capacity of the local healthcare network.

  - Prompting spontaneous or organized migrations away from the affected area towards other areas whose health systems’ capacity may be overwhelmed by the new arrivals.

  - Increasing the potential risk of a critical outbreak of communicable or psychological diseases among the affected population.

  - Causing food shortages that lead to malnutrition and undermine resistance to various diseases.

Table 4 lists the most common effects of the natural hazards considered in this handbook:

|  | Table 4 Likely Effects of Various Natural Hazards |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Effect | Earthquakes | Strong Winds | Tsunamis and Flash floods | Ordinary Floods | Landslides | Volcanic and Lahar Activity |
| Loss of lives | High | Low | High | Low | High | High |
| Severe injuries requiring complex treatment | High | Moderate | Low | Low | Low | Low |
| Major risk of communicable diseases | Potential risk following all significant phenomena (Likelihood increases with crowding and the degradation of sanitary conditions) |  |  |  |  |  |
| Damage to health facilities | Severe (structure and equipment) | Severe | Severe but localized | Severe (equipment only) | Severe but localized | Severe (structure and equipment) |
| Damage to water supply systems | Severe | Light | Severe | Light | Severe but localized | Severe |
| Food scarcity | Infrequent (generally caused by economic or logistical factors) |  | Common | Common | Infrequent | Infrequent |
| Large migrations | Infrequent (common in severely affected urban areas) |  | Common (Generally limited) |  |  |  |

| Source | : | Vigilancia Epidemiológica Sanitaria en Situaciones de Desastre, guía para el nivel local, Pan American Health Organization, 2002. |
| --- | --- | --- |

The interruption of a health facility’s operations after a disaster may be short-term (hours or days), or long-term (months and years). It all depends on the magnitude of the event and its effects on the sector. Magnitude cannot be controlled; its consequences, however, can be.

When it comes to a future health facility, the effects of these phenomena can be controlled if site selection is guided by sound information and criteria, and the design, construction, and maintenance can withstand local hazards. For instance, Concepción’s Main Hospital in the south of Chile managed to continue operating in spite of being near the epicenter of the country’s most devastating earthquake of the 20th Century, which took place on 21-22 May 1960.

Failures are, by and large, more widely publicized than successes—but the Concepción case is by no means exceptional. Another example worth noting is the vastly different behavior of two hospitals, located right next to each other, that were hit by the Northridge earthquake of 1994. The first, USC Medical Center Hospital, had been designed employing a seismic protection system called base isolation. Not only did it suffer no structural damage, but none of its equipment or key contents was overturned in the quake, and the facility remained in operation throughout the crisis and beyond.  The other, adjacent facility had been designed and built according to traditional standards.  Its damage was so severe it could not continue to operate, and it was eventually demolished.

- Economic aspects

Several reports by the United Nations Economic Commission for Latin America and the Caribbean (ECLAC) has published state unequivocally that natural disasters are a significant obstacle to the economic and social development of the countries in the region. While adverse natural phenomena do not discriminate between industrialized and developing countries, their consequences can be very different. In 1998, for instance, 95 percent of the deaths associated with natural disasters took place in developing countries. There, adverse natural phenomena are far more likely to devastate the population’s standard of living and their development prospects. By contrast, natural phenomena generally affect only marginally the economy and population of developed countries.  (See Table 5).

| Table 5 Effect of Natural Disasters On National Economies |  |  |  |
| --- | --- | --- | --- |
| Location | Event | Date | Effect on the Economy |
| Managua, Nicaragua | Earthquake, 7.2 on the Richter scale | 1972 | Fall of 15 percent in GDP and 46 percent in Managua’s industrial and productive activity. |
| Mexico | Earthquake, 8.1 on the Richter scale | 1985 | GDP fell by 2.7 percent |
| Nicaragua | Hurricane Joan | 1988 | GDP suffered an additional 2 percent reduction, 17 percent in the agricultural sector. |
| Ecuador | Floods caused by the El Niño Phenomenon | 1997-1998 | GDP growth 1.2 percent lower than expected in 1998. |
| Dominican Republic | Hurricane Georges | 1998 | GDP reduction of 1 percent compared to annual forecast. |
| Nicaragua | Hurricane Mitch | 1998 | GDP growth of 4 percent, 1.1 points lower than forecast for that year. |
| Honduras | Hurricane Mitch | 1998 | Fall in GDP of 7.5 percent. |

| Source: | ECLAC/IDB, A Matter of Development: How to Reduce Vulnerability in the Face of Natural Disasters, prepared for the “Confronting Natural disasters: A Matter of Development” Seminar, 2000 |
| --- | --- |

The effects of a natural disaster are amplified in the health sector, for several reasons: first, it is one of the sectors that tend to suffer important economic losses in such situations, given the significant investments required; second, its recovery also implies large outlays, difficult to procure at a time when the rest of the country is also trying to recover; and third, it needs to quickly recover its capacity, not only to continue meeting the normal demand for its services, but also to care for the population directly affected by the event.

- Disaster vulnerability reduction in health facilities

In recent years, after hurricane Mitch and the major El Salvador earthquakes, several countries, among them Argentina, Bolivia, Chile, Colombia, Costa Rica, Honduras and Peru, and international institutions such as PAHO/WHO, ECLAC, the Inter-American Development Bank (IDB) and the World Bank, have begun to raise awareness concerning the need to promote strategies for mitigating the vulnerability and managing the risks facing health systems in the region. Considerable progress has been made in the field of disaster education in medicine and nursing faculties, in schools of architecture and engineering. The lessons learned reveal that most of the losses in health infrastructure were due to location in vulnerable areas, inadequate design, or the lack of proper maintenance. While most efforts have focused on assessing and reducing the vulnerability of existing health facilities, in recent years a new and encouraging trend has taken hold: investing in new infrastructure based on investment or functional protection criteria. In Chile, for instance, starting in 1999, it is mandatory for project consultancy groups to include specialists in hospital vulnerability, whose role it is to ensure that performance criteria are incorporated into the design and construction of new health infrastructure.

The Pan American Health Organization, through its Public Health in the Americas initiative, has defined a set of Essential Public Health Functions (EPHF). Aimed at the health authorities of the region at all levels—central, intermediate, and local—they set the foundation for evaluating the current healthcare situation, improving public health practices, and strengthening the leadership of sanitary authorities. Among the essential functions agreed upon in June 2000, during the 126th session of PAHO’s Executive Committee, is reducing the impact of emergencies and disasters on health, which is to be achieved through the following actions:

- The planning and execution of public health policies and activities regarding prevention, mitigation, preparedness, response, and early rehabilitation.

- A multiple focus that addresses the threats and etiology of all possible emergencies or disasters that can affect a country.

- Participation of the entire health system, and the broadest possible intersectoral cooperation, in reducing the impact of emergencies and disasters on healthcare.

- The promotion of intersectoral and international cooperation in finding solutions to the health problems caused by emergencies and disasters.

- Objectives and scope of this handbook

The experience of several countries revelas that is possible to employ a methodology for the design and construction of new health facilities that is capable not only of ensuring the safety of human lives, as has been the case, but also of ensuring the safety of the investment in the facility and its continued operation as well. Depending on the characteristics of the health network and the economic resources available, it is strategically possible to build health facilities that enjoy a high level of functional and investment protection.  While no one can demand that such facilities remain perfectly intact and fully functional both during and immediately after a severe emergency, it is reasonable to expect them to recover in a reasonably short time, and at a reasonable cost.  Finally, if resources are limited or the natural or technical conditions do not allow it, health facilities can still be built that, confronted with severe natural phenomena, can suffer moderate or even considerable damage without imperiling the lives of their occupants—much as is the case now.

In order to meet the new and more ambitious performance objectives, it is necessary to establish new design and construction criteria—and engage in quality assurance from start to finish. Experience shows that the financial cost of applying these measures represents less than 4 percent of the total construction cost, and in some cases is practically zero since it only implies choosing a different location or changing the underlying design philosophy. In any case, the amount is marginal when compared to the economic costs of retrofitting or rehabilitating a structure damaged by a natural disaster—not to mention the social, political and economic impact of the temporary or permanent loss of a health facility.

The traditional stages in the project development cycle for the construction of new health facilities are the following:

Preinvestment:

Stage I: Identity of the need for a new health facility. At this stage, consideration is made of variables such as the characteristics of the existing healthcare network, current development policies, the rate of utilization of existing services, expected demand, epidemiological and demographic profiles, health policies, and geographical characteristics of the area. Directly associated with this stage is the search for financing for the development of the new facility.

Stage II: Assessment of options to meet this need. At this stage the various options for meeting the need for a new health facility are identified, assessed, and compared. The definitive location of the facility is an essential variable in this process.

Stage III: Medical architectural program and preliminary plans. In this stage the services and spaces desired are defined and preliminary plans are drafted in order to determine the functional relations and basic characteristics of the new infrastructure.

Investment:

Stage IV: Project design. In this stage the project plans, specifications, budget, and tender documents are drawn up.

Stage V: Construction. At this stage, the new infrastructure comes into physical existence.

Operations:

Stage VI: Operations and maintenance. While this stage is not part of the development of the new infrastructure, it is indispensable that in the previous stages the way the facility will operate and remain functional is defined in advance.

The chief purpose of this handbook is to assist health sector administrators and professionals whose mission is the management, design, construction, and inspection of new hospitals, laboratories, and blood banks with a view to protecting the operation of these facilities and the investment made in them. With this in mind, the new characteristics of the project development stages will be described in the pages that follow, and the procedures for selecting the performance objective will be specified.  We will also discuss how to assess the various siting, design, and construction options, as well as how to select the professional teams that will be involved in the project. While this handbook is not a design or building code, relevant basic concepts will be presented, and reference will be made to specific documents where one can find the appropriate technical recommendations needed to meet the performance objective desired.

In drafting this handbook, only some natural hazards have been taken into account: seismic events, hurricanes and strong winds, landslides, floods, and volcanic eruptions.  Other phenomena—such as drought, fire, or man-made hazards—have been excluded, either because they are unlikely to damage the facility’s operation or investment, or because they are adequately covered elsewhere.

It is also important to acknowledge that different natural phenomena present different challenges to the development of the project. In the case of floods or volcanic activity, generally the only technically and financially feasible option is to select a site that offers the desired level of safety. If landslides, mudslides, or floods are the prevailing hazards, it is often possible to modify the variables that control the phenomenon—for instance, by engaging in extensive tree planting, or building ditches and other water-diversion structures. When it comes to seismic events, hurricanes and strong winds, it is necessary, in addition to correctly choosing the site, to design the structures so that they are resistant to such phenomena. In the specific case of earthquakes, it is necessary to provide safety to the entire infrastructure, both internal and external. In the case of strong winds, protection efforts focus mainly on exposed external components. In extreme situations, the only solution is to distribute the risk by building not one facility but several, distributed spatially, that can perform the desired healthcare functions. Being located in different sites should improve the odds of effective protection, since even if some of them are affected, functional damage will not be total. Being aware of these differences and options should facilitate appropriate and cost-effective risk management.

- Definition of basic concepts

Below, concepts of a general nature are defined to assist the reader.  Definitions of more specific concepts will be presented further on, as part of the relevant chapters.

| Natural hazard | An event of natural origin and sufficient intensity to cause damage in a particular place at a particular time. |
| --- | --- |
| As-built Report | Set of documents concerning project managers, contractual documents, the professionals involved in regional and local risk assessments, the design of the project, construction and inspection procedures, applicable codes and standards, certificates of component safety, final plans for the structure, its components and protection systems, and certificates of compliance with project specifications. |
| Structural components | Elements that are part of the resistant system of the structure, such as columns, beams, walls, foundations, and slabs. |
| Non-structural components | Elements that are not part of the resistant system of the structure. They include architectural elements and the equipment and systems needed for operating the facility. Among the most important non-structural components: architectural elements such as façades, interior partitions, roofing structures, and appendages. Non-structural systems and components include lifelines; industrial, medical and laboratory equipment; furnishings; electrical distribution systems; HVAC systems; and vertical transport systems |
| Structural detailing | A set of measures, based on the theoretical, empirical and experimental experience of the various participating disciplines, for protecting and improving the structural component performance. |
| Non-structural detailing | A set of measures, based on the theoretical, empirical and experimental experience of the various disciplines, aimed at protecting and improving the non-structural component performance. |
| Tender documents | Legal documents that stipulate the characteristics of the design or building contract or contracts (parties involved, financial amounts, deadlines, forms of payment, etc.) and the technical characteristics of the construction (general and detail plans, structural and non-structural components, standards and codes that must be followed, specialized inspection requirements, recommended and unacceptable construction methods, etc.). |
| Specialized inspection | Activities aimed at ensuring that the requirements of the project are met in matters such as quality of the work, the use of construction processes and materials of a quality commensurate with the goals of the project, the fulfillment of the provisions established in the standards and codes referenced in the contracts, and the procurement of component safety certificates and others. |
| Quality assurance | A set of actions aimed at ensuring that project performance objectives are met. |
| # Risk | Extent of the likely losses in the event of a natural disaster. The level of risk is intimately associated with the level of protection incorporated into the structure. |
| Critical services | Services that are life saving, involve hazardous or harmful equipment or materials, or whose failure may generate chaos and confusion among patients or the staff. |
| Resistant system | A structural system especially designed to withstand the impact of natural phenomena. The structural system must be designed in such a way that its detailing is proportional to the performance objective chosen for the structure. |
| Protection systems | Devices and procedures aimed at providing safety to the structural and non-structural components of the building and meeting the performance objective. |
| Vulnerability | The likelihood of a facility that enjoys a particular level of protection suffering material damage or being affected in its operations when exposed to a natural hazard. |

Chapter II

Protecting the Healthcare System

- Introduction

The consequences of a disaster on a health facility are not restricted to the panic that may ensue among the staff and patients, or total or partial damage to its structure.  They may also include the partial or total loss of the operational capacity of the facility and, therefore, its capacity to meet and alleviate healthcare demand at the very moment the local community most urgently needs such services. Moreover, the technical and economic restrictions generally faced by the health sector hinder its prompt recovery. It is not unusual for hospitals to continue smarting from the impact of a natural disaster 10 years or more after its occurence.

At present technological advances, as well as changes in design philosophy and quality assurance regarding the construction and maintenance of health infrastructure, make it possible to limit the damage caused by disasters and set different performance levels for investment and functional protection.  However, it is not always possible to reach high protection levels. Natural or technical restrictions, such as the need for a health facility on a small island with considerable volcanic activity and a substantial population, or economic restrictions, when the need to expand the system to meet health targets clashes with the need to ensure the safety of the facilities, can compromise the desirable performance objective.  Finally, there are political restrictions, such as the need to build on a site that will please a given constituency.

Although economic resources may be limited, and particular situations may impose technical restrictions on the fulfillment of higher performance objectives, a detailed assessment is still required to ensure the optimal utilization of available resources. The starting point should be a clear overview of the existing health network, including its operational characteristics, spatial distribution, the degree to which it complies with health policies and meets health targets, the epidemiological and demographic profile of the population, and the natural hazards that threaten it. The real functional capacity of all existing health network facilities must be assessed, taking into account to the fullest extent possible all actual data regarding the natural hazards they must contend with, and their current level of vulnerability.

Once the actual characteristics of the healthcare network have been identified, and the need to build a new health facility within this network in a specific location has been established, it is necessary to define the role that the new facility will be called on to play, both in normal times and during emergencies of various kinds and intensities.

Based on the role required with respect to various natural and other hazards, the level of overall functional performance must be set for each specific health facility—that is to say, whether it is meant to continue providing services as smoothly as possible during the emergency, or whether the criterion is for the structure to withstand the disaster in such a way that recovery and rehabilitation can take place after a reasonably brief interruption. The level of overall performance is a function of the level of protection selected for each one of the services provided. All this will have a bearing on the characteristics of the site, the specifics of the infrastructure to be built, and the basic services it can realistically be expected to provide based on different scenarios. (See Flow Chart 1).

In practical terms, three broad performance objectives can be listed: functional protection, investment protection, and life safety.

| Life safety | The minimum requirement for any infrastructure, and the criterion most commonly used in the design and construction of health facilities. |
| --- | --- |
| Investment protection | The protection of all, or at the very least the key components of, the health facility’s infrastructure and equipment, even if the facility itself cannot continue to function. Based on this criterion, it is possible to design and build infrastructure that can restart operations within a reasonable time—although not immediately—at a cost that can be met by the Institution. |
| Functional protection | Investment protection is implicit in this objective, which in addition calls for the construction of systems that can remain operational during a disaster or recover their functional capacity in a relatively short time. |

The approach hereby proposed, which focuses on setting performance objectives for each of the services to be provided by the facility, given the various hazards present in the region and their likely intensity, calls for two potential intensity levels to be considered when designing a facility: the traditional design level for each hazard, and a maximum credible scenario, which would call for exceptional protection measures. Although not always practicable, basing the protection strategy on the latter scenario is the most desirable approach.  In the case of earthquakes, for instance, the minimum protection level should shield the facility from a seismic event with a 10 percent probability of exceedance over a 50- year period. On the other hand, the high-protection level would withstand an earthquake so exceptionally strong that it would only have a two- percent probability of exceedance in 50 years.

Flow chart 1

Definition of Performance Objective

Form 1

Definition of Protection objectives

In order to sensitize all project participants concerning the need for disaster mitigation, it is advisable that the various stakeholders agree in writing on the performance objective to be met, defining protection goals for the facility in normal times and in the event of various disaster scenarios. Form 1 may help in this awareness-raising effort.  One should be filled for each hazard present in the area where the infrastructure will be sited.

- Basic services

The overall performance objective for the facility is directly related to the level of protection that its services will require. Tables 6A and B list some of the medical and support services for which protection levels should be set. The level of protection must be aligned with the overall performance objective desired for the facility; however, is not necessary that all services should enjoy the same level of protection defined overall for the entire facility.

| #### Table 6a Typical Medical Services in a Hospital |  |  |
| --- | --- | --- |
| Blood Bank | Internal Medicine | Pediatric Neurology |
| Cardiology | Kinesiotherapy | Pediatric Surgery |
| Dental Services | Laboratory | Pediatrics |
| Dermatology | Neonatology | Pharmacy |
| Ear, Nose and Throat | Nuclear Medicine | Plastic Surgery - Burns |
| Emergencies – Adults | Obstetrics and Gynecology | Pneumology |
| Emergencies – Children | Oncology | Psychiatry |
| Endoscopy | Ophthalmology | Recovery Rooms |
| General Inpatient Care | Orthopedics and Traumatology | Sterilization |
| Hemodyalisis | Other Medical Services | Surgery |
| ICU/ITU | Outpatient Clinic | Surgical Wings |
| Imaging, Diagnostic | Pathological Anatomy | Urology |

| #### Table 6b Typical Support Services and Systems |  |  |
| --- | --- | --- |
| Administration | Escape Routes | Non-sterile Materials Storage |
| Air Conditioning (HVAC) | Filing and Case Management | Oxygen System |
| Boilers, Thermal Power Station | Fire Alarm/Suppression System | Powerhouse |
| Clinical Gases | Food Services | Sewerage |
| Communications | Industrial Gases | Sterile Materials Store-Rooms |
| Drinking Water | Industrial Water | Vertical Transport System |
| Electrical Distribution | Laundry | Other Support Services, Systems |
| Emergency Standby Electrical System | Mobilization and Transport |  |

- Classification of medical and support services

In order to select correctly the performance objective for each service, it is advisable to consider the the risks to which it is exposed, the activities it involves, the characteristics of its components, and its relative importance.

| Critical Services and Systems | Must be classified as specified below |
| --- | --- |
| Critical services involving life-saving or other essential functions | Those services that must remain in operation to meet the vital healthcare needs of current in patients and provide first aid and other services to the victims of the disaster. Also included in this group: those services whose failure could cause prolonged delays in the recovery of critical functions. |
| Critical services involving hazardous or harmful materials | Damage to these services increases the risk of fires, explosions, air pollution, or water contamination that could injure the staff, patients, or visitors. |
| Critical services whose failure may cause the patients or staff to panic | Those services whose failure may cause alarm, chaos or confusion among the staff, patients, or visitors to such a degree that the quality or even the provision of health care may be compromised. |
| Special Services and Systems | Services that, without being critical, involve components that would be difficult or expensive to replace. |
| Other Services and Systems | Those services whose contents can suffer minor failure that can be repaired quickly and does not lead to prolonged interruptions or significant decreases in healthcare quality. |

- Protection levels required for each service

Just as a performance objective must be set for the facility as a whole, its services and support systems should also be classified in accordance with the performance goals and various hazard scenarios that may affect them.

| Functional Protection (FP) | The facility is able to operate normally immediately—or nearly so—after an emergency. Losses in functional capacity, if any, are temporary and do not endanger patients or staff. To meet this goal, infrastructural (structural and non-structural) components and organizational or functional components must perform with a similar degree of success. Such components are only allowed a limited degree of damage. The functional protection objective implicitly incorporates the investment protection and life-safety performance objectives. |
| --- | --- |
| Investment protection (IP) | At this intermediate level of protection, the goal is to prevent damage to the infrastructure of those services that it would be difficult or costly to replace. To meet this goal, both the structural and the non-structural components must perform similarly. In some cases, investment protection may result indirectly in functional protection. |
| Life Safety (LS) | It is acceptable for the service to suffer considerable damage to its structural or non-structural components as long as such damage does not put lives at risk. As a result, it may be necessary to carry out significant repairs after the disaster. Such repairs may be economically impracticable. |

Depending on the classification of each service based on the importance of the activities and components involved, performance objectives such as those recommended in Table 7 should be set.

| Table 7 Performance Objectives for the Various Services |  |  |  |
| --- | --- | --- | --- |
| Classification of the Service | Performance objective |  |  |
|  | FP | IP | LS |
| ## Critical services |  |  |  |
| ### Vital or essential |  |  |  |
| Hazardous or harmful |  |  |  |
| Likely to cause chaos or confusion |  |  |  |
| Special Services |  |  |  |
| Other Services |  |  |  |

The protection goals contained in the table above may be redefined, as agreed upon by the Project Coordination Team, depending on the economic capacity of the Institution and the project’s role and importance within the overall health network.

- Definition and characterization of the performance objectives for infrastructural components

Once a performance objective has been set for the facility as a whole, as well as for each of its services, it should determine the organizational, safety, and control performance criteria for the prevention or mitigation of any damage to infrastructural components.

Infrastructure is typically divided into two groups: the structure, and the non-structural elements. The structure comprises all those essential elements that determine the overall safety of the system, such as beams, columns, slabs, walls, braces, or foundations. The non-structural elements are those that ultimately enable the facility to operate; they are divided into architectural elements, equipment and content, and services or lifelines. A reasonable level of protection for the non-structural components of each service should be chosen.

| Functional Protection of Components (FPC) | The structural system must perform in such a way that the building can continue to be used safely both during, and immediately after, an adverse event. The structural elements must remain nearly as rigid and resistant as before the emergency. Any damage that occurs should be minimal, with no repairs required for operational continuity (what is known as controlled damage). Non-structural components should continue to perform their functions without alteration, both during and after the emergency. Any damage should be minimal and allow for the continuing occupation of the premises. |
| --- | --- |
| Investment Protection of Components (IPC) | Damage to the structural system is acceptable so long as the replacement of service components is not unduly arduous or expensive. It should be possible to repair any damage that occurs at reasonable expense and in a short period of time, so as to minimize interference with the functions ordinarily performed. |
| Life-Safety Protection of Components (LPC) | Damage to structural and non-structural components is acceptable so long as it does not endanger the patients, visitors, or employees. Repairs may be expensive and interfere severely with the operations of the facility in the medium and even long term. |

The performance objective for any component must be at least equal to the performance objective set for the overall service to which it belongs, or with which it interacts.

- Setting the performance objective for each service

Form 2 may be used to set the performance objective for the health facility and the services it provides. This form should be filled jointly by the Institution’s representatives and the professionals involved in the design and execution of the project. A similar form should be filled for each likely disaster scenario and each level of protection contemplated.

- Degree of detail of the project

The performance objective set for the facility, together with the risk level estimated by the multidisciplinary group of specialists who participated in its conception, should determine the degree of detail with which the project is to be designed. Broadly speaking, two levels of detail may be considered—each having significant implications for the site studies to be carried out, the design procedures to be followed, or the qualifications of the professionals hired to build the project or practice quality assurance. Table 8 shows the available options in relation to the performance objective chosen.

| Table 8 Level of Detail of the Required Studies |  |  |  |
| --- | --- | --- | --- |
| Performance Objective |  | Level of risk |  |
|  |  | High | Low |
| Functional protection |  | D | D |
| Investment protection |  | D | B |
| Life safety |  | D | B |
|  | D : Detailed Study |  |  |
|  | B : Basic Study |  |  |

Table 9 summarizes the main characteristics of the studies referred to in the previous table.

| Table 9 Characterization of the Project |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  |  | Level of Detail of the Study |  |
|  |  |  | Detailed Study | Basic Study |
| Requirements that must be met by the participating professional teams |  |  | (See Chapter V) | (See Chapter V) |
| Studies required |  |  |  |  |
| Identity of siting options |  |  |  |  |
| Compilation of hazard information at the regional level |  |  |  |  |
| Compilation of hazard information at the local level for each of the potential sites |  |  |  |  |
| Definition of facility protection options |  |  |  |  |
| Identity of services requiring protection |  |  |  |  |
| Define level of protection for the various services and their components |  |  | See Table 7 | See Table 7 |
| Protection systems’ design requirements for structural components, non-structural components, and medical and industrial equipment |  |  |  |  |
| Requirements based on national and international standards |  |  |  |  |
| Requirements specific to the project or to health facilities in general |  |  |  |  |
| Expected results |  |  |  |  |
| Detail plans |  |  |  |  |
| Technical specifications |  |  |  |  |
| Tender documents |  |  |  |  |
| Certificates (See Table 19b) |  |  |  |  |
| Calculation logs (See Table 19a) |  |  |  |  |
| Typical Completion schedule 1 |  |  | 8-12 months | 6-10 months |
| Quality assurance program for the project (See Chapter VI) |  |  |  |  |
| Notes: | 1 | The completion schedules are only meant to serve as examples. The duration of any given study will depend, among other variables, on the dimensions and performance objective of the facility and the natural hazards prevalent in the area. |  |  |

Form 2

- References

Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000.

Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001.

Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986.

Departments of The Army, The Navy and The Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988.

Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Assessment of Existing Buildings, Washington, D.C., 1998.

Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000.

Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994.

Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001.

U.S. Army Corps of Engineers, Engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998.

Chapter III

General Criteria for Selecting a Safe Site

- Introduction

The identity of siting options and the selection of the definitive site for the facility must be based on an assessment of the healthcare needs of the population and the characteristics of the existing health network. The choice of site will also be affected by public health policies and any demographic, geographical, sociopolitical or economic criteria set by the institution. Other important considerations are the performance objectives sought for the facility at normal times and during emergencies, the comparative analysis of the natural and technological hazards present at the various potential sites, the estimated cost and technical feasibility of implementing the necessary protection systems, the economic resources available, and the findings of the cost/benefit analysis of the options as illustrated in Flowcharts 2 and 3.

This assessment must cover not only the specific sites but also their surroundings. The way in which natural phenomena affect the surrounding population, the population of reference and the infrastructure must be evaluated, particularly their impact on lifelines and access roads.

Flow chart 2

Site preselection

SITE PRESELECTION HEALTH, SOCIAL, POLITICAL AND ECONOMIC CONSIDERATIONS SITE C SITE A SITE B SELECTION OF DEFINITIVE SITE IDENTITY ● RISK ASSESSMENT ● POTENTIAL COST ASSESSMENT OF THE SITING OPTION ● ASSESSMENT OF TECHNICAL RESTRICTIONS ● ASSESSMENT OF SITE ADVANTAGES ● COST/BENEFIT ANALYSIS IDENTITY ● RISK ASSESSMENT ● POTENTIAL COST ASSESSMENT OF THE SITING OPTION ● ASSESSMENT OF TECHNICAL RESTRICTIONS ● ASSESSMENT OF SITE ADVANTAGES ● COST/BENEFIT ANALYSIS IDENTITY ● RISK ASSESSMENT ● POTENTIAL COST ASSESSMENT OF THE SITING OPTION ● ASSESSMENT OF TECHNICAL RESTRICTIONS ● ASSESSMENT OF SITE ADVANTAGES ● COST/BENEFIT ANALYSIS

Flow chart 3

Site selection

SITE SELECTION TECHNICAL RESTRICTIONS - HEALTHCARE NEEDS - ECONOMIC RESTRICTIONS CHARACTERISTICS OF HEALTH NETWORK SOCIAL AND POLITICAL RESTRICTIONS SOCIAL AND POLITICAL REQUIREMENTS TECHNOLOGICAL HAZARDS NATURAL HAZARDS PERFORMANCE OBJECTIVES IN NORMAL TIMES PERFORMANCE OBJECTIVES DURING EMERGENCIES

- Process for selecting siting options

  - Variables of site selection

It is not the purpose of this handbook to show in detail how to rank the various siting options.  Instead, relevant criteria will be mentioned, such as the key factors that must be taken into account when selecting an adequate and safe location. It is advisable that the Institution define qualitative and quantitative specifications for assessing and comparing each of the siting options. These specifications may be of varying degrees of complexity. What matters is that they facilitate the decision-making process by testing each site’s capacity to meet the desired performance objective. If none of the siting options can meet it, it will be necessary to select a less ambitious performance objective—or continue searching for acceptable siting options.

All the information on local risks that may be needed for choosing the siting options might be limited to existing data found in land-use management plans, local or regional development plans, technical reports, local zoning laws and regulations, or the opinions of experts. Even so, on-site inspection of each of the options and their surroundings should be carried out by the Assessment and Selection Team. If the health facility will be designed to meet a high performance objective, however, detailed studies must be carried out to characterize the prevailing hazards. No site should be selected if any of the detailed information required is lacking.

In selecting the site, moreover, one must consider the proximity to certain industrial facilities (chemical plants, refineries, mining processing plants, etc.), military facilities, landfills, airports, routes used for the transport of hazardous materials, and so on, facilities that—because of their operations, the emission of toxic agents, or the possibility of eventual accidents at normal times or during an emergency—might affect the safety of the contemplated health facility.

An aspect worth considering is the feasibility of having the local regulatory plan modified in such a way that no activities can be carried out in the future that endanger the hospital and its operations.

  - Site selection procedures

The selection of the site involves three stages, each with its own activities or substages.

Stage 1: Compilation of background data

Stage 2: Assessment of siting options

Stage 3: Site selection

2.2.1	Stage 1: Compilation of background data

2.2.1.1	Preliminary studies

When the different siting options have been selected by the Client Institution, it will be necessary to evaluate any background data available concerning each of the options. The team in charge of site selection must determine whether the available data are sufficient or more information is required in order to compare the various options and select the definitive site. Table 10 lists some of the activities that should be carried out at this stage.

#### Table 10 #### Preliminary activities

Selection of professional team (see Chapter V)

##### Definition of protection objectives and expected level of damage

##### Definition of siting options

Delimitation of the boundaries within which the potential sites would be located

Area to be occupied by the facility

Area of influence

Roads

Lifelines

###### Review of local regulatory plans

Preliminary studies

Human settlements and infrastructure in the region

Inhabited area

Services

Roads and available forms of transportation

Review of existing laws and regulations

Review of regional development plans

Review of existing cartography

Review of general information regarding the sites of interest and their surroundings

Review of background data regarding adverse natural phenomena that have taken place in the region, such as landslides or mudslides, strong winds, floods, seismic events or volcanic eruptions

Compilation of preliminary geotechnical data regarding the potential sites

Compilation of information gathered for other projects that have been developed in the area

Opinion of government bodies and NGOs

Opinion of experts

At this stage, the team of specialists participating in the project must estimate the probability of occurrence of the various natural phenomena considered in this handbook. This is necessary in order to define the level of detail of the studies required to characterize the hazards in the sites chosen. In case not enough information is available, or there are doubts regarding that information, the team of specialists must inform the Project Director and Coordination Team and recommend which studies are needed to characterize the prevailing hazards on each site. The level of detail of the studies will also be determined, naturally, by the performance objective chosen for the facility (see Table 8).

      - Studies required for assessing the risks prevalent in each of the siting options

At the beginning of this stage, the team of specialists must evaluate if the information compiled during the preliminary stage is sufficient to preselect the best potential sites for the facility. If it is, the next step is to carry out a closer evaluation of the siting options, as discussed further on in this chapter. If the information required is not available, the team of specialists must carry out all studies necessary for producing the information that will characterize the hazards prevalent in each site. An example of the types of studies required can be found in Annex A.

2.2.2	Stage 2: Assessment of the siting options

2.2.2.1	Processing the data

The information compiled during the preliminary studies, or that obtained later as needed, must be processed in order to characterize the hazards and level of risk at each of the siting options. Flow chart 4 summarizes the main variables that must be quantified in order to determine the natural hazards prevalent at each site.

Flow chart 4

Quantification of the Risk

QUANTIFICATION OF PREVAILING RISKS EARTHQUAKE DIMENSIONS MAGNITUDE DURATION LIKELIHOOD AFFECTED AREA CHARACTERIZATION DESIGN SPECTRUM SEISMIC VERIFICATION RECORDS DIRECT GEOTECHINICAL CONSEQUENCES MITIGATION POTENTIAL SNOW DIMENSIONS MAGNITUDE DURATION LIKELIHOOD AFFECTED AREA CHARACTERIZATION DESIGN LOAD MITIGATION POTENTIAL STRONG WINDS DIMENSIONS MAGNITUDE DURATION LIKELIHOOD AFFECTED AREA CHARACTERIZATION DESIGN SPEED MITIGATION POTENTIAL LANDSLIDES & MUDSLIDES DIMENSIONS MAGNITUDE DURATION LIKELIHOOD AFFECTED AREA CHARACTERIZATION VOLUME HEIGHT SPEED MITIGATION POTENTIAL FLOODS DIMENSIONS MAGNITUDE DURATION LIKELIHOOD AFFECTED AREA CHARACTERIZATION VOLUME HEIGHT SPEED MITIGATION POTENTIAL VOLCANISM DIMENSIONS MAGNITUDE DURATION LIKELIHOOD CHARACTERIZATION VOLUME SPEED MITIGATION POTENTIAL

To obtain the results summarized in the chart above the tasks specified in tables 11a through 11f must be carried out.

#### Table 11a #### Assessment of landslide risk

Assessment of conditions for the occurrence of a landslide

Historical background

Vegetation

Geological conditions

Natural strata

Topographical conditions

Steepness of slopes

Geomechanical conditions

Stratigraphic sections

Strata of low cohesion and low shear-strength soil

Soil and rock degradation

Watercourse-related hazards (destabilization)

Seismic hazard

Human intervention

Assessment of slope stability

Preliminary assessment

Detailed assessment

Dimensions of the risk of landslides

Surface affected and volume displaced

Velocity of the landslide

Safety factors

Likelihood

Production of landslide risk maps (microzoning)

#### Table 11b #### Assessment of mudslide risk

Assessment of conditions for the occurrence of mudslides

Historical background

Meteorological conditions

Vegetation

Geological conditions

Naturally unstable strata

Topographical conditions

Steepness of slopes

Geomechanical conditions

Stratigraphic sections

Low-cohesion soil with low shear strength

Soil and rock degradation

Drainage and permeability

Human intervention

Dimensions of the risk of mudslides

Surface affected and volume of material displaced

Mudslide speed

Likelihood

Production of mudslide risk maps (microzoning)

#### Table 11c #### Assessment of the risk of strong winds

Assessment of conditions for the occurrence of strong winds

Historical background

Meteorological conditions

Topographical conditions

Dimensions of the risk of strong winds

Wind speed

Likelihood

Production of wind speed maps (microzoning)

#### Table 11d #### Assessment of flood risk

Assessment of conditions for the occurrence of floods

Historical background

Meteorological conditions

Existence of watercourses in the area

Topographical conditions (low-lying areas)

Permeability and use of the soil

Risk of flood by tsunami

Human intervention

Identity of critical points – Calculation of hydraulic axes

Identity of critical overflow points during floods

Dimensions of the risk of flooding

Surface affected

Height of flood water level

Flow speed

Likelihood

Production of flood risk maps (microzoning)

#### Table 11e #### Assessment of seismic risk

Characterization of seismogenic conditions

Establishment of frequency-magnitude ratios

Estimation of the maximum probable seismic event

Estimation of seismic risk

Probabilistic seismic hazard analysis

Definition of attenuation factors

Estimation of the duration of strong ground motion

Estimation of the predominant period of ground motion

Deterministic seismic hazard analysis

Dimensions of the seismic risk

Linear response spectrum

Foundation-soil liquefaction potential

Likelihood of massive landslide (See section on landslides)

Likelihood of tsunamis (See section on floods)

Production of seismic risk maps for each of the siting options

#### Table 11f #### Assessment of volcanic risk

Assessment of likelihood of volcanic activity

Likelihood of lateral explosions

Likelihood of being in the path of pyroclastic flows

Likelihood of being in the path of lava flows

Likelihood of massive landslides

Likelihood of mudslides

Likelihood of contamination by gases and ashes

Likelihood of solid and particulate matter emissions

Likelihood of tsunamis

Dimensions of the risk of volcanic activity

Surface affected (area of influence of volcanic action)

Velocity of the flows

Degree of toxicity of gases emitted

Magnitude of related ground motion

Characterization of probable mudslides (See section on mudslides)

Characterization of probable floods due to tsunamis (See section on floods)

Likelihood

Production of volcanic risk maps (microzoning)

2.2.2.2	Technical and economic feasibility of protection systems

In the case of each likely natural hazard, the technical and economic feasibility of implementing overall protection systems for the structure through the execution of peripheral works and other actions must be evaluated.  The following table lists some of these actions.

#### Table 12 #### Actions that can assist in the overall protection of the facility

Strategies for protection against landslides and mudslides

Slope stabilization

Soil stabilization through the use of geotextiles

Knocking down unstable masses

Reforestation

Cleaning natural watercourses, canals

Construction of drainage facilities

Construction of alluvial terraces

Constant monitoring (instrumentation); early warning systems

Strategies for protection against strong winds

Production of technical detailing specifications

Reforestation

Permanent monitoring of meteorological conditions; early warning systems

Strategies for flood protection

Construction of protection barriers at critical points of the watercourse

Construction of gavions [retaining walls made of rocks and chicken wire] along the full length of the watercourse

Cleaning natural watercourses and canals

Construction of drainage facilities

Reassessment and improvement of rainwater collection and drainage

Reinforcement of the structural system

Others

Strategies for seismic protection

Production of technical specifications for seismic-resistant design

Strategies for protection against volcanic activity

# Permanent monitoring and early warning system

2.2.2.3	Impact of hazards on the sites under consideration

In the case of each prevailing hazard, an assessment must be made of its likely impact on the population to be served, as well as on local lifelines, related agencies, and overall access to health services. The likely impact of the phenomenon on the health network of the region—and, where appropriate, of the country—must also be assessed. This assessment should not only consider the network’s infrastructure but also the functional, economic, and political aspects. All too often, while damage to health infrastructure may be manageable from a technical viewpoint, the political impact can be devastating.

2.2.3	Stage 3: Site selection

2.2.3.1	Selection of the best option

The information compiled must be processed in order to select the safest and most convenient site for the facility. Table 13 summarizes the minimum activities required for the selection of the best site.

#### Table 13 #### Site selection

Production and superimposition of hazard data

Assessment of the level of risk at each of the siting options

Characterization of the hazards present at each site

Cost assessment for the overall protection of the structure

Cost assessment for the protection of key services, systems and components

Vulnerability assessment (likely impact of each hazard)

Comparative cost/benefit analysis of the various options

Selection of definitive site for the structure

In some circumstances it is not possible to meet the desired performance objective due to the extreme conditions in which the target population is forced to live. Given the lack of safe locations, the project’s performance standards should guide siting choices in ways such as the following:

- Dividing the functions of the facility in such a way that they are carried out in different locations that are remote from each other.

- Procuring mobile or temporary facilities.

- Producing effective reference systems so that the population can easily be transferred to health facilities in other areas.

These options make it possible to distribute or reduce the risk.  They also increase costs and make operations more complex than might be desired, but may be the only reasonable alternative if the level of risk is too great.

      - Production of document summaries

The information obtained during the preliminary stage through the risk assessments and the process of site selection must be summarized in a document that should include, at the very least, the following content:

- Explanation of the reasons for the choice of site.

- Description of the risks identified in the site.

- Causes of those risks.

- Characterization of the risks.

- Design recommendations for the facility, including the length of time it can remain cut off from basic services (water, electricity, etc.).

- Design and protection recommendations for the area of influence.

- Protection objectives for the health facility.

- Assessment of site safety

Form 3 below should assist the Project Director and the Coordination Team in selecting a safe site for the hospital.

Form 3

- References

ASCE 7-98, Minimum Design Loads for Buildings and Other Structures, American Society of Civil Engineers, 1998.

FEMA 55: Coastal Construction Manual, Federal Emergency Management Agency, Washington, 1996.

Hallent, B., Photogrammetry: Basic Principles and General Survey, McGraw-Hill, 1960.

Key, D., Structures to Withstand Disasters, Thomas Telford, London, 1995.

Kuroiwa, J., Reducción de Desastres: Viviendo en Armonía con la Naturaleza, Lima, 2002.

Ministry of Housing and Urban Development, Planificación de Asentamientos Humanos en Zonas Propensas a Desastres, Chile, 1982.

PAHO/WHO Collaborating Center for Disaster Mitigation in Health Facilities, Bases Metodológicas: Evaluación de Vulnerabilidad Sísmica de Edificaciones Estructuradas con Pórticos de Preformed concrete, Evaluación de Elementos Arquitectónicos y Evaluación de Equipamiento, University of Chile, 2000.

Pan American Health Organization, Manual para la Mitigación de Desastres Naturales en Sistemas Rurales de Agua Potable, 2001.

Pan American Health Organization, Natural Disaster Mitigation in Drinking Water and Sewerage Systems: Guidelines for Vulnerability Analysis, 2000.

Pan-American Health Organization, Disaster Mitigation for Health Facilities: Guidelines for Vulnerability Appraisal and Reduction in the Caribbean, 2000.

Simiu, E., Wind Effects on Structures: an Introduction to Wind Engineering, John Wiley & Sons, 1978.

Taype, V., “Aplicación de Mapas Geodinámicos en la Prevención de Desastres Naturales”, Fourth National Simposium on the Prevention and Mitigation of Natural Disasters, Lima, CISMID, 1990.

Chapter IV

Design and Construction of the Project

- Introduction

After selecting the correct site for the facility, it is time to design a project that provides a level of safety commensurate with the performance objective chosen. The protection systems to be used for this purpose must meet two requirements: it must be feasible to build them, and it must not be difficult to provide them with an effective level of maintenance. A poor design will lead to constraints during the other stages of the project that could make it difficult, even impossible, to meet the performance objective.

The acceptable level of damage to the structural and non-structural components of the facility is directly related to the time—and expense—needed for recovery, as defined by the Institution for the various hazards and levels of risk. Table 14 shows the acceptable levels of damage to the facility’s components in terms of the recovery time for different degrees of risk. While recovery times cannot be guaranteed in advance, the matter must be addressed effectively, since it corresponds to the Institution’s very real need to predict when it will be able to start providing its services again during an emergency.

| Table 14 Acceptable Levels of Damage to Components1 |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Intensity of the Hazard |  | Acceptable Level of Damage |  |
| Recovery time | Credible Maximum Desired | Minimum Recommended | Structural Components | Non-structural Components |
| Immediate (Hours) |  |  | Minor | Minor |
| Short (Weeks) |  |  | Minor to Moderate | Minor to Moderate |
| Moderate (Months) |  |  | Moderate | Moderate |
| Long (More than one Year) |  |  | Moderate to Severe | Severe |
| Very Long (Or Never) |  |  | Severe | Not Considered |

| Notes : | 1 | Annex B contains a series of tables, adapted from FEMA 356, listing accepted levels of damage to structural and non-structural components in the event of a “design” earthquake (one two-thirds of the intensity of the maximum considered earthquake, or MCE), based on two different performance objectives for the structural system. |
| --- | --- | --- |

The design process involves seven clearly differentiated stages:

- Drafting of a Medical Architectural Program.

- Selection of the Preliminary plan Development Team.

- Drafting of the Preliminary plan.

- Selection of the Project Development Team.

- Development of the Project.

- Selection of the General Contractor.

- Construction.

In order to implement these stages, it is vital for the Client Institution, which sets the goals and requirements, to act rigorously in the selection of two main teams:

- The Execution Team, which carries out the various tasks required at each stage.

- The Reviewing Team, whose job is quality assurance in compliance with the project goals and needs of the Client Institution.

Chapter V describes the various types of professionals that need to be involved in the project, and the criteria they must meet. As part of the quality assurance strategy, it is necessary to underscore the role played by the Reviewing Team in ensuring that the performance objective is actually met. The Team must establish up coordination mechanisms that can effectively evaluate the implementation of the project and the incorporation of the agreed-upon protection measures. At each stage of the design process, and for each service to be provided, the Team must evaluate whether the performance objective has been achieved.

- Stages in the design and construction of the facility

2.1.	Stage 1: Preliminary Plan

The design process has, as its starting point, a Medical Architectural Program, defined by the Institution, which stipulates the services the new facility will provide and the physical space it will require to do so. The Program typically specifies all the services to be provided, the functional areas needed, and the desired dimensions in square meters. It is on the basis of this Program that the Preliminary Plan will be drafted, and which will define how the services and spaces will be handled. This process must include the definition of the physical characteristics of the facility and its operation.

Taking into consideration the hazards the facility may face, it will be necessary to choose protection methods and systems that can meet the challenges posed by these hazards. For instance, in areas of high seismicity, buildings must be regular in their geometric plan and elevation, and systems that do not lead to sharp deviations in the structural system must be selected. In addition, it is desirable at this stage to establish whether there will be constraints on the form and distribution of the facility as a result of the structure’s protection systems. For instance, if a seismic base isolation system is used, a discontinuity at the isolation interface will be required not only throughout the entire floor plan but also in the immediate perimeter areas, in order to accommodate any displacements that may occur. This situation compels the use of special designs that must be considered at this stage. Likewise, in high-wind areas, the type of roof covering and façade elements is highly relevant. In flood-prone areas, meanwhile, it may be necessary to employ fills above the level of reference that would normally not be considered.

Usually, more than one preliminary plan will be produced for each facility. The selection of the definitive plan, in addition to any functional and aesthetic considerations that may influence the final choice, should be guided by how thoroughly the existing regional and local risks have been taken into account, along with the necessary solutions to secure the performance objective set for the project. Table 15 should be of help in assessing any preliminary plan in terms of the performance objective set for the facility.

Table 15 Preliminary Plan Selection

Prevalent Hazards:

Ways in which those hazards may affect the facility

Ways in which the preliminary plan takes the effects of the various hazards into account

Location

Shape

Structural system, and level and type of protection

Dependence on external services and agencies

Special protection elements contemplated

Particular design considerations

Measures to ensure that the performance objective will be met

Since it is during the Preliminary Plan stage that the requirements of the Medical Architectural Program will be interpreted, and formal solutions found for the protection challenges it poses, it is essential that the Execution Team have enough experience to perform this correctly.

2.2.	Stage 2: Selection of the Design Team

This is the time to define the requirements that must be met by the specialists who will develop the definitive project, and to select the various work groups.

2.3.	Stage 3: Design

The first step in this stage is to to carry out the detailed studies needed for the production of the definitive project, which will consist of technical specifications, plans, mockups, and tender documents (see Flow Chart 5).

Due to the additional complexity of any health facility in comparison with ordinary bldgs without the same stringest occupancy requirements, a large number of professionals (grouped by discipline as specified in Table 24) must participate. Each team of specialists will be in charge of developing a specific subproject: the structure, the heating, ventilation and air conditioning (HVAC) system, the various support services, and so on. Coordination is required for all these activities, and therefore clear procedures and protocols must be defined for the generation and sharing of information. Appropriate coordination is the key to the successful completion of this stage.

From the point of view of vulnerability reduction and the fulfillment of the performance objective, the Design Coordination Team must advise each of the specialized work groups on the functional and protection requirements specified for the facility and its services. Each team of specialists will be called on to prepare a document in which it clearly explains how it will achieve these objectives and, most importantly, what their requirements and restrictions will be in relation to the other disciplines in order to meet these objectives.

The design of the project will be the result of the integration of the work of all the participating disciplines on each section of the contemplated facility, so it bears repeating that coordination is indispensable. The safety criteria chosen for each section has to be the same across all disciplines, and the ways in which they will be met must be established in advance by all teams. The protection systems that will be incorporated must then be included in the construction documents outlining the physical details of the system to be built: the technical specifications and the various plans.

#### Flow Chart 5

Design of the Project

DESIGN SELECTION OF DISCIPLINES/DESIGN GROUPS WORK BY TEAM OF SPECIALISTS 1 PROJECT: PLANS SPECIFICATIONS MOCKUPS BUDGET TENDER DETAILS OTHER DOCUMENTS VERIFICATION OF THE FULFILLMENT OF THE PERFORMANCE OBJECTIVE TENDER DEFINITION OF WORK PLANS AND QUALITY ASSURANCE ADEQUATE INADEQUATE QUALITY ASSURANCE VULNERABILITY CONTROL ASSURANCE WORK BY TEAM OF SPECIALISTS 2 WORK TEAM OF SPECIALISTS 3

When considering the overall safety of the infrastructure in question, it is common to classify its components into two groups: the structure itself, and the non-structural elements. Generally, the design team in charge of the structure is proficient in two disciplines: structural engineering and architecture. In the design of the non-structural elements, all disciplines must be equally involved.

2.3.1.	Design of the structure

      - Characteristics of the structural design

The structural system must meet the performance objectives defined for the facility as a whole and the services it will provide. The structural engineering team is chiefly responsible for the safety of the structure. When the performance objectives of the facility and its services call for investment and functional protection, the team must provide a structural system that not only safeguards the structure itself but also the non-structural elements. Put differently, the structure not only must protect—it must make it feasible to implement procedures for protecting the non-structural systems. For this reason, the structural system needs to be approved by all the disciplines represented in the project.

At present, non-traditional structural systems provide different levels of safety both for the structure and the non-structural elements. For instance, in the case of seismic demand, several hospitals have been built successfully employing seismic base isolation systems, which create an interface between the foundations and the structure through the use of rubber or friction-pendulum bearings that simulate a car’s suspension system. Such systems keep the seismic energy from reaching the structure through dissipation, reducing significantly the impact of strong ground motion on the structure and non-structural elements.

The structural system and its components must be designed to withstand the permanent and potential forces that affect a structure, including its dead load (its own weight) as well as its live load (the structure in operation), its seismic load, wind load, snow or ash load, temperature changes, hydrostatic and hydrodynamic soil factors, total and relative settlements of foundations, and so on, all of which are defined and regulated by existing design standards.

In general terms, the design must incorporate structural detailing that can effectively meet the protection objective for each level of risk. It is also important to incorporate in the design any systems that, in case of damage and functional losses, may enable the facility’s services to recover within a predefined timeframe.

Given the materials that are employed in construction, there will always be some degree of damage. For instance, damage to reinforced concrete buildings may present itself as fissures, cracking, or the partial or total collapse of the material. However, no level of damage is acceptable if it put the lives of the users or staff at risk. To the fullest extent possible, moreover, situations must be prevented that can cause panic among the staff and the evacuation of the facility when it is technically unnecessary.

The following form summarizes the aspects that must be evaluated by the Design Coordination Team in order to verify that a level of safety adequate to the design of the structural system has been incorporated.

Form 4

      - Information provided by the Structural Design Team

The Structural Design Team must request, and later provide, the information required by the other disciplines for the design of the equipment, systems, and other non-structural components. Table 16 illustrates some of the data that must be exchanged.

Table 16 Information that must be provided by the Structural Design Team

Story drift ratio

Forces acting on the points of support

Acceleration at each story

Others (Specify)

The Project Coordination Team must ensure that this information is taken into account by all the other disciplines working on the design of the project.

      - Safety assessment of the structural system

The specialists in charge of the structural design of the facility must be able to guarantee that the protection criteria set by the institution will be met. The following forms, included for illustrative purposes only, list the minimum background data that must be assessed by each of the specialist teams if seismic or high-wind hazards are present at the facility’s intended site.

Form 5

Form 6

2.3.2.	The design of non-structural components

2.3.2.1	Characteristics of the design of non-structural components

Non-structural elements are those components that, while not being part of the resistant system of the structure, are crucial to the effective operation of the facility. In the case of hospitals, close to 80 percent of the total bill for the facility goes into non-structural components, among them architectural elements, medical and laboratory equipment, office equipment, electrical and mechanical-industrial equipment, distributed lines, and basic installations.

The impact of damage to the facility’s non-structural components may vary. For instance, damage to medical equipment or to the lifelines that supply medical and support services can actually cause loss of lives or—what often amounts to the same thing—the loss of the functional capacity of the facility. While less dramatic, partial or total damage to certain components, equipment, or systems may entail prohibitive repair and replacement costs. Major damage to systems, components, or equipment containing or involving harmful or hazardous materials may force the evacuation of some parts of the facility, resulting in a loss of operational capacity.

Secondary effects of the damage to non-structural components are also important, for instance the fall of debris in hallways or escape routes, fires or explosions, or the rupture of water or sewerage pipes. Even relatively minor damage, it should be stressed, can compromise aseptic conditions in the affected areas, putting critical patients at risk.

Non-structural components must incorporate a level of protection that is proportional to the performance objective that has been defined for the medical or support service in question, as well as all other services that are directly or indirectly related to them. Each team of specialists must be responsible for the design of the protection systems required by the components of their competence, and must certify, by following the procedures described in section 2.3.2.2, that the performance objective defined by the institution has been met.

The Project Coordination Team must ensure that the subprojects designed by the various disciplines are correctly integrated and compatible with each other, and it should hold regular coordination meetings in which representatives of each team are present. Moreover, the Coordination Team will be responsible for ensuring that each work group is provided in timely fashion with the most up-to-date information regarding the work of the other teams and the overall progress of the project.

Table 17 and Form 7 should assist the Project Coordination Team in verifying that protection systems are being effectively incorporated in the various non-structural components that typically require protection.

| Table 17 Typical Non-structural Components that Require Protection |  |  |
| --- | --- | --- |
| Architectural | Equipment and Furnishings | Basic facilities |
| Partitions | Medical equipment | Medical gases |
| Interiors | Industrial equipment | Industrial gas |
| Façades | Office equipment | Electric distribution |
| Suspended ceilings | Furniture | Telecommunications |
| Roofs or decks | Contents | Vacuum |
| Cornices | Supplies | Drinking water |
| Terraces | Clinical files | Industrial water |
| Chimneys | Pharmacy shelves | Air conditioning |
| Plaster |  | Steam |
| Glass windows |  | Piping in general |
| Appendages |  |  |
| Canopies |  |  |
| Antennas |  |  |

| Source: | Boroschek, R. and Astroza, M. Disaster mitigation in Health facilities: Non-structural Aspects, Pan American Health Organization, 2000. |
| --- | --- |

The protection of non-structural systems calls for a logical sequence: first, interior safety and the stipulation of requirements for the immediate exterior (characteristics of supports, anchoring, etc.); secondly, the safety of the immediate exterior (furnishings, ceilings, supplies and others); and, finally, the safety of the overall structure. The following table summarizes the main ways to protect non-structural components:

| Table 18 Main Forms of Protection |  |  |  |
| --- | --- | --- | --- |
| Non-structural Component to Protect | Protection Provided by: |  |  |
|  | Structure | Architecture | Furnishings |
| Architectural |  |  |  |
| Industrial equipment |  |  |  |
| Medical and laboratory equipment |  |  |  |
| Distributed systems |  |  |  |

Form 7

2.3.2.2	Assessing the safety of non-structural components

Non-structural components require protection systems that can guarantee the achievement of the performance objective set for the project. Assessing the degree to which the protection goals for the different disaster scenarios have been met may be done in several ways, most commonly through mathematical modeling or certificates issued by the supplier or manufacturer of the component or system.

Tables 19a and 19b summarize the procedures that each discipline must follow in order to assess potential protection systems.

#### Table 19a #### Safety Assessment of Systems, Equipment and Non-structural Components through Mathematical Analysis1

Minimum required content of Calculation Log2

Identity of the specialist

Name of the specialist

Discipline

Classification of the system, equipment or component

Architectural element

Lifeline

Medical or laboratory equipment

Industrial equipment

Isolated electrical or mechanical equipment

Distributed electrical or mechanical equipment

Level of protection under consideration

# Performance objective for the overall facility and the area where the system, equipment or component is located

Performance objective for the services supported by the system, equipment or component

Performance objective for the system, equipment or component itself

Standards considered in the analysis

National standards

International standards

Other standards specific to the project

Description of the structure where the system, equipment or component will be located

Geometrical dimensions

Number of stories

Height of stories

Estimated load of the various stories of the building

Essential facts on the dynamic properties of the building

Other essential facts

Behavior determining the response of the system, equipment or component

Interior safety

Support element or anchoring

Anchoring

Bracing

Stability (overturning, sliding)

Deformation

Resistance

Highest level of damage tolerated

Interaction with other elements

Dependence on other elements

Other (specify)

Description of the system, equipment or component

General description, function, and dependence on other systems, equipment or components

Weight, distribution of the weight, and location of the center of mass in different conditions of use and operation

Geometrical dimensions

Chief materials and mechanical characteristics

Support systems

With vibration isolation system

Without vibration isolation system

Detail plans or sketches

Interior safety certificate issued by the supplier or manufacturer

Background facts on performance in previous emergencies

Description of built-in protection systems

Systems used for the interior safety of the component

Systems used to increase the safety to the support element

Systems used for anchoring and stabilization

Systems used for damage control

Systems used to prevent interaction with other components

Other systems used to provide safety to the system, equipment or component

Characteristics of the equipment when in operation (Evaluate only relevant equipment)

Frequency of operation

Storage capacity

Loads produced during the operation of the equipment

Operational temperature

Operation in corrosive environment

Identity of least favorable actions and load combinations 3

Bracing characteristics of systems, equipment and components

Description of the structural concept

Degree of Inclination of the braces

Length of the braces

Profile section of braces

Thickness of the bracing element

Capacity of the material

Elasticity of the material

Distance between braces

Detail plans

Anchorage characteristics of systems, equipment and components

Description of the structural concept

Resistance of the materials

Number of anchoring elements

Diameter of the anchoring elements

Embedded length of the anchoring elements

Plans of the anchoring elements

Characteristics of system, equipment or component support elements

Material

Shape of the elements

Resistance of the materials

Other characteristics of the support elements

Classification of the system, equipment or component

Fundamental period To

Rigid equipment or component

High deformability

Limited deformability

Low deformability

Flexible equipment or component

High deformability

Limited deformability

Low deformability

Spatial distribution

Isolated element

Distributed element

Number of points of support

Response

Sensitive to acceleration

Sensitive to deformation

Contents

Hazardous or difficult-to-replace materials

Materials not dangerous nor difficult to replace

Interaction with other systems, equipment and components

Not linked

Linked

Dependence on other systems, equipment and components

Independent

Dependent

Other relevant classifications

Method of analysis

Equipment included in structure analysis model

Equipment not included in structure analysis model

Static analysis

Dynamic analysis

Characteristics of the demand

Summary of factors that determine the demand

Return period associated with the expected demand

Damping considered

Factors that may modify the response

Demand as it is considered in the design

Results

Internal efforts

Utilization factors of bracing elements

Utilization factors of anchoring elements

Estimated deformation

Assessment of the system, equipment or component’s bracing or anchoring elements

Stability

Assessment of interaction with other systems, equipment or components

Assessment of potential impacts

Assessment of potential contamination by hazardous or harmful materials

Confirmation that Objectives have been met

| Notes: | 1 | The table above applies to architectural elements, industrial equipment, medical and laboratory equipment, lifelines and other components of the services that need to be protected. In the case of each item, the data regarding the equipment or component analyzed should be evaluated individually. |
| --- | --- | --- |
|  | 2 | The calculation log should include all computational processes and the results of the intermediate calculations. |
|  | 3 | In addition to the load caused by the potential emergency--the dead load, the live load, the load caused by the failure of the equipment, the load associated with electrical or mechanical failure, the load derived from the interaction with other equipment or components, and the load stipulated in the contract standards. |

#### Table 19b #### Standardized Safety Assessment of Systems, Equipment and Non-structural Components through Certification by the Supplier or Manufacturer1

Analysis-based Certification

A calculation log must be attached covering the contents specified in 19a, in accordance with the level of detail required by the study. This document will be used for reviewing the safety of the component

Experimental Certification

Identity of accredited laboratory

Standards of reference employed in the tests

Description of test procedures

Demand applied in the tests

Results of the tests

Certification Requirements

Conditions of use and operation

Conditions of installation

Other conditions

Date of certification and validity of the certification

Certification of compliance with standards specified in the contract

Description of limitations and applicability of the certification

| Notes: | 1 | The previous table applies to architectural elements, industrial equipment, medical and laboratory equipment, lifelines and other standard components related to the services that will be protected. |
| --- | --- | --- |

2.3.2.3	Safety assessment of non-structural components

The various teams of specialists must guarantee that the performance objective set for the project has been met. The following form, included for illustrative purposes only, lists the minimum background data that must be taken into consideration by each of the disciplines:

Form 8

The design stage concludes with the production of the final plans, technical specifications, mockups, budgets of reference, and tender documents. At this stage, both the Design Execution Team and the Project Reviewing Team must deliver a document certifying that the Protection Objective has been met.

2.4.	Stage 4: Selection of the General Contractor

The selection of the General Contractor who will engage in the actual construction of the facility must meet all relevant national legislation and standards. Among the selection criteria, the experience of candidate firms in the building of disaster-resistant health facilities should be considered. Chapter V describes the requirements that must be met by the companies interested in bidding for the contract.

2.5.	Stage 5: Construction

It is at this stage that the performance objective set for the facility must be realized. Quality assurance Procedures such as those mentioned in Chapter VI must now be rigorously followed in order to ensure that protection goals are met.

While the project’s specifications and plans should guide the construction process, in practice it is often necessary to introduce modifications or clarify the meaning of certain requirements. In such situations, any request for modifications presented by the Contractor must be meticulously evaluated, and any alteration to the original plans should be approved by the Client Institution, the Design Team, and the Reviewing Team. Modifications to the facility’s performance objective must be subjected to careful analysis and discussion, which needs to be documented—thereby ensuring that the facility’s real operational capacity within the overall health network has been correctly determined.

- References

  - Standards, codes and general protection reference material

American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures.

Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000.

Building Officials Code Administrators International, International Building Code 2000.

Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001.

Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988.

Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981.

European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998.

Federal Emergency Management Agency, FEMA 276: Example Applications of the NEHRP Guidelines for the Seismic Rehabilitation of Buildings, Washington, D.C., April 1999.

Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Assessment of Existing Buildings, Washington, D.C., 1998.

Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000.

Federal Emergency Management Agency, FEMA 55: Coastal Construction Manual.

Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, TO Practical Guide, Washington, D.C., September 1994.

International Standards Organization, ISO 3010:2001: Basis for Design of Structures—Seismic Actions on Structures.

International Standards Organization, ISO 4354:1997: Wind Actions on Structures.

Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001.

U.S. Army Corps of Engineers, Engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998.

  - Standards, codes and references specific to protection of structural components and non-structural.

Tables 20 and 21 show examples of specific standards, codes and references that may be considered in the design of the protection systems of the structural and non-structural components.

| Table 20 Protection of Structural Components |  |
| --- | --- |
| Natural hazard | Standards, Codes and References Specific to Design and Analysis |
| Strong winds | American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures. Building Officials Code Administrators International, International Building Code 2000. Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981. European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998. Federal Emergency Management Agency, FEMA 55: Coastal Construction Manual. Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994. International Standards Organization, ISO 4354:1997: Wind Actions on Structures. |
| Seismic event | American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures. Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000. Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001. Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001. Building Officials Code Administrators International, International Building Code 2000. Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986. Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988. Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981. European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998. Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994. Federal Emergency Management Agency, FEMA 276: Example Applications of the NEHRP Guidelines for the Seismic Rehabilitation of Buildings, Washington, D.C., April 1999. Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Assessment of Existing Buildings, Washington, D.C., 1998. Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000. International Standards Organization, ISO 3010:2001: Basis for Design of Structures—Seismic Actions on Structures. Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001. U.S. Army Corps of Engineers, engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998. |

| Table 21 Protection of Non-structural Components |  |  |
| --- | --- | --- |
| Non-structural Component | Standards, Codes and References Specific to Design and Analysis | Professional Team Required |
| Isolated (not distributed) electrical and mechanical equipment Industrial equipment | American Petroleum Institute, API 650: Welded Steel Tanks for Oil Storage, Washington, D.C. Deutsches Institut für Normung, DIN IN 61587-2: Mechanical Structures for Electronic Equipment - Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks (IEC 61587-2:2000), 2001. Ishiyama, Y., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. Institute of Electrical and Electronic Engineers, IEEE C 37.81: Guide for Seismic Qualification of Class 1E Metal-Enclosed Power Switchgear Assemblies, New York, 1989. Institute of Electrical and Electronic Engineers, IEEE C 37.98: Seismic Testing of Relays, New York, 1987. Institute of Electrical and Electronic Engineers, IEEE 344-1987: Recommended Practice for Seismic Qualification of Class 1E Equipment for Nuclear Power Generating Stations, New York, 1987. International Electrotechnical Commission, IEC 60068-3-3: Environmental Testing – Part 3, Seismic Test Methods for Equipment, 1991. International Electrotechnical Commission, IEC 60255-21-3: Electrical relays - Part 21: Vibration, Shock, Bump and Seismic Tests on Measuring Relays and Protection Equipment - Section 3: Seismic Tests, 1988. International Electrotechnical Commission, IEC 61166-21-2: High-Voltage Alternating Current Circuit-Breakers - Guide for Seismic Qualification of High-Voltage Alternating Current Circuit-Breakers, 1993. International Electrotechnical Commission, IEC 62271-002: Amendment 1 to IEC 61166: Gas-Insulated Metal-Enclosed Switchgear for Rated Voltages of 72.5 kV and Above - Guide for Seismic Qualification. International Electrotechnical Commission, IEC/TS 61463: Bushings - Seismic Qualification, 2000. International Electrotechnical Commission, IEC 61587-2: Mechanical Structures for Electronic Equipment – Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks. Ishiyama, Y.., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. | Electrical engineer Mechanical engineer Seismic engineer Structural engineer Vulnerability assessment specialist Hospital architect Industrial equipment specialist |
| Pipes, ducts and electrical conduit systems Fire safety systems | National Fire Protection Association, NFPA 13: Standard for the Installation of Sprinklers Systems. Sheet Metal and Air Conditioning Contractors National Association, Seismic Restraint Manual: Guidelines for Mechanical Systems & Addendum Nº1. WSP 029, Aseismic Design Manual for Underground Steel Water Pipelines, 1989. | Electrical engineer Mechanical engineer Seismic engineer Structural engineer Vulnerability assessment specialist Fire Protection Specialist |
| Medical and laboratory equipment Furniture | International Electrotechnical Commission, IEC 60068-3-3: Environmental Testing - Part 3: Guidance. Seismic Test Methods for Equipment, 1991. Ishiyama, Y., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. | Hospital architect Medical equipment specialist Seismic engineer Structural engineer Vulnerability assessment specialist Furniture designer |
| Systems of Suspended ceilings Lighting fixtures Systems | American Society for Testing and Materials, ASTM E 580: Standard Practice for Application of Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels in Areas Requiring Moderate Seismic Restraint, 2000. Ceilings and Interior Systems Construction Association, Guidelines for Seismic Restraint, Direct Hung Suspended Ceilings Assemblies: Seismic Zones 3-4, 1991. Uniform Building Code Standard 25-2: Metal Suspension Systems for Acoustical Tile and for Lay-in Panel Ceiling. | Hospital architect Specialist lighting fixtures Seismic engineer Structural engineer Vulnerability assessment specialist |
| Vertical transport systems | American Society of Mechanical Engineers, ASME A17.1: Safety Code for Elevators and Escalators, 1996. Deutsches Institut für Normung, DIN IN 61587-2: Mechanical Structures for Electronic Equipment - Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks (IEC 61587-2:2000), 2001. Japanese Elevator Association, Guide for Earthquake Resistant Design and Construction of Vertical Transportation. Standard New Zealand, NZS 4332:1997: Non Domestic Passenger and Goods Lifts. 1997. | Vertical transport specialist Mechanical engineer Electrical engineer Seismic engineer Structural engineer Vulnerability assessment specialist |
| Roofing structures | Federal Emergency Management Agency, Against the Wind. | Hospital architect Seismic engineer Structural engineer Vulnerability assessment specialist |
| Partitions and façade elements | American Architectural Manufacturers Association, Aluminum Curtain Wall Design Guide Manual American Architectural Manufacturers Association, Aluminum Store Front and Entrance Manual American Architectural Manufacturers Association, Design Windloads for Buildings and Boundary Layer Wind Tunnel Testing American Architectural Manufacturers Association, Installation of Aluminum Curtain Walls American Architectural Manufacturers Association, Maximum Allowable Deflection of Framing Systems for Building Cladding Components at Design Wind Loads American Architectural Manufacturers Association, Metal Curtain Wall Fasteners American Architectural Manufacturers Association, Metal Curtain Wall Manual American Architectural Manufacturers Association, Rain Penetration Control – Applying Current Knowledge American Architectural Manufacturers Association, Structural Design Guidelines for Aluminum Framed Skylights American Architectural Manufacturers Association, Voluntary Specifications for Hurricane Impact and Cycle Testing of Fenestration Products. Federal Emergency Management Agency, Against the Wind. | Hospital architect Seismic engineer Structural engineer Vulnerability assessment specialist |
| Doors and windows | American Architectural Manufacturers Association, Glass and Glazing. Federal Emergency Management Agency, Against the Wind. International Standards Organization, ISO 6612:1980: Windows and Door Height Windows Wind Resistance Tests. | Hospital architect Structural engineer |

Chapter V

Assessment of the Work Team

- Professional requirements

A key aspect of quality assurance, especially in the case of health facilities with high protection requirements, is the selection of experienced professional teams who remain active and up to date in the field. For this reason, the selection of the professionals and firms that will conceive and make the project a reality must be based on an objective appraisal of their qualifications, such as their professional level, the number of projects completed, the square meters that have effectively been built, and their previous participation in health sector projects.

1.1	Specialists required for the preliminary-stage and hazard assessments

The preliminary stage of the project, including the hazard and risk assessments, calls for the hiring of professionals in the fields listed in table 22.

| Table 22 Professionals Required for Hazard Assessment |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Natural Hazards |  |  |  |  |  |
| Professionals Needed | Mudslides | Landslides | Hurricanes | Floods | Seismic events | Volcanic eruptions |
| Urban Development Specialists |  |  |  |  |  |  |
| Topographers |  |  |  |  |  |  |
| Geologists |  |  |  |  |  |  |
| Soil Mechanics Specialists |  |  |  |  |  |  |
| Meteorologists |  |  |  |  |  |  |
| Hydrologists |  |  |  |  |  |  |
| Hydraulic Engineers |  |  |  |  |  |  |
| Seismologists |  |  |  |  |  |  |
| Wind Engineers (specialized in hydrodynamics) |  |  |  |  |  |  |
| Seismic Engineers |  |  |  |  |  |  |
| Structural Engineers |  |  |  |  |  |  |
| Volcanologists |  |  |  |  |  |  |

These professionals must be selected in compliance with the criteria defined in Table 23.

It cannot reasonably be demanded that the disaster vulnerability assessment specialists have previous experience in the design of hospital infrastructure. Nevertheless, it would be useful if they had. On the other hand, experience in hazard and risk assessments is indispensable.

Table 23 Professional Requirements for Team Involved in Preliminary Plan and Design of the Facility

| Position | Minimum Certified Experience | Experience in Hospital Design (Last 10 Years) |  |
| --- | --- | --- | --- |
|  |  | Total Surface Built | Other Requirements |
| Director | 10 years | > 150,000 m2 | At least 2 Hospitals with Surface Built > 10.000 m2 |
| Coordination Team | 10 years | > 150,000 m2 | At least 2 Hospitals with Surface Built > 10.000 m2 |
| Specialists | 10 Years | > 100,000 m2 | At least 1 Hospital with Surface Built > 10.000 m2 |
| Risk Assessment Specialists | 10 years | - | - |
| Assistants | 5 years | - | - |

  - Specialists required for the preliminary plan, design, construction and inspection of the project

The Preliminary Plan Team, the Coordination Team, the participating specialists, and the Building Contractor must show that they have at least 10 years’ experience in the design, construction and inspection of health infrastructure, not only generally but with specific reference to the role they intend to play in the construction fo the new health facility.

Some of the key disciplines that must participate in the design, construction, and inspection of the project are listed in Table 24.

| Table 24 Specialists Required for the Design, Construction and Technical Inspection of the Works1 |  |  |
| --- | --- | --- |
| Air conditioning3 | Geotechnical engineering | Structural design4 |
| Architecture2 | Industrial equipment5 | Telecommunications8 |
| Budgeting and finance | Lighting fixtures | Vertical transport |
| Built-in furnishings | Medical and laboratory equipment | Vulnerability |
| Clinical gases | Medical furnishings | Waste management |
| Construction methods | Medicine and nursing | Water treatment9 |
| Electrical installations | Pneumatic mail | Other (specify) |
| Fire safety7 | Sanitary facilities6 |  |
| General safety | Signage |  |

| Notes: | 1 | The professionals whose disciplines are listed on this table must be selected according to the criteria defined in Table 23. The professionals in charge of the design, construction and technical inspection of the works must prove that their experience is in keeping with the goals of the project. |
| --- | --- | --- |
|  | 2 | The architect must carry out or supervise the safe design of the structural components of his or her competence, including façade elements, interior partitions, suspended ceilings, and appendages. |
|  | 3 | Included in this discipline: A/C systems, heating, ventilation, etc. |
|  | 4 | Depending on the conditions of the contract, the specialist must carry out the structural review of the non-structural components’ protection systems. |
|  | 5 | Included in this discipline: laundry, food or dietary services, sterilization, etc. |
|  | 6 | Included in this discipline: drinking water and sewerage networks, natural gas, etc. |
|  | 7 | Included in this discipline: dry and wet networks, sprinklers, etc. |
|  | 8 | Included in this discipline: closed-circuit TV, telephony, internal communications, etc. |
|  | 9 | Included in this discipline: Dialysis, boiler room, sterilization, laboratory, etc. |

- Criteria for the selection of the Execution Team and other consultants

The following tables specify the information that must be presented and certified by the specialists and consultancy firms that aspire to participate in the project:

Table 25a Information Required of Consultancy Firms

General Information

Identity of the potential contractor

Full name of the company

Legal domicile

Year of incorporation

Articles of incorporation

Legal representative

Business license

Contractor’s management and professional staff (incl. subcontractors, if applicable)

Name

Professional or technical degree

Professional or technical discipline

Position in the company (if applicable)

Academic and government certificates

Current activities and projects underway

Company cash flow and credit status

Average annual financial revenues and other resources, in dollars

Average annual profits from projects done in the past 5 years, in dollars

Banking and credit references

Table 25b Requirements that Must Be Met by Consultancy Firms

Technical Requirements

Certified company experience (works or services)

Project name

Project client

Project field (according to table 25c)

Economic value of the project

Built surface of the project

Total surface of the project

Execution period

Disciplines involved

Technologies employed

Standards and codes applied

Experience in similar projects

Certified experience of all relevant specialized staff

Project name

Project client

Economic value of the project

Built surface of the project

Total surface of the project

Execution period

Professional field

Project director

Project manager

Specialist

Designer

Assistant

Other

Activities carried out by the professional (only those that can be certified)

Field (as specified in Table 25c)

Disciplines applied

Experience in similar projects

Standards and codes applied

Listing of equipment, machinery, and tools to be employed

Other technical requirements that the institution or coordination team consider relevant for the execution of the project.

#### Table 25c #### Project Areas

Planning and feasibility

Administration

Basic engineering assessments

Engineering

Architecture and urban planning

Construction

Inspection

Miscellaneous evaluations and assessments

- Assessment of the Work Team

Form 9

Chapter VI

Project Quality Assurance Procedures

1.    Guiding principles for the review and inspection of the project

The following table lists some of the basic principles that must be heeded in order to ensure the quality of the project, including review and inspection mechanisms at each stage to ensure the meeting of Performance Objectives.

Table 26 Basic Principles that Should Guide the Review and Inspection of the Project

- A high performance objective calls for a high degree of specialization among project participants. Special attention must be paid to the analysis and detailing of the components, as well as to building practices and the meticulous inspection of the construction process. - Design and construction should meet the principles and quality criteria of the ISO9000 standard. - At each stage of the project, participating specialists must review the work underway to make sure it meets the standards of their particular discipline. In addition, they should engage in interdisciplinary reviews across disciplines as a form of double-checking. - At each stage of the project (including both design and construction), independent inspections must be carried out. The specialists in charge of the design and construction of the facility must carry out their activities in full awareness that such inspections will take place. - Before the final plans are issued for each of the components or disciplines, a draft must be issued to the various teams of specialists for review and commentary. - All quality standards that the project requires must be documented. No tacit or oral agreements will be accepted. - The Technical Inspection Team must comprise a multidisciplinary group of specialists with expertise proportional to the overall protection requirements of the project. The team must include at least one representative from each of the disciplines listed in table 24. - The Technical Inspection Team must guarantee that all the provisions stipulated in the tender documents are met. - The Technical Inspection Team must make every effort to ensure that its role is preventive rather than corrective. - Each standard system, equipment, or component must be certified to meet the performance objectives of the project. - Any modification to the original project during the construction stage must be approved by all the parties: the Client Institution, the Project Director, the Coordination Team, the specialists, the Technical Inspection Team, and the Contractor. The characteristics of the modification must be described in detail in the As-built Report. - Materials, systems or equipment defined in the project specifications may be replaced by a technical equivalent proposed by the Contractor, subject to the prior approval of all the parties. The characteristics of the technical equivalent must be clearly described in the As-built Report. - Any project involving operational or investment protection objectives calls for an As-built Report. In projects where the performance objective only calls for the safety of the occupants, an As-Built Report must be produced if expressly demanded by the institution or the Coordination Team. - Other principles should be applied if the work group considers them necessary or relevant.

- Project Quality Assurance during the Preliminary and Design Stages

The following table specifies the tasks required for the correct execution of the project in its preliminary stage, including regional and local hazard studies, as well as its design phase.

#### Table 27 #### Quality Assurance Program for the Initial and Design Stages of the Project

#### Project Definition

#### Definition of the objectives and scope of the project

#### Definition of the Participants (see Chapter V)1

#### The Client Institution

#### The Project Director

#### The Planning and Coordination Team

#### The specialists that will integrate the Project Execution Team

#### Participating consultancy firms and other participating firms

#### The Review Team, with representatives from each of the relevant disciplines

#### Assignment of functions and responsibilities, and limits thereof1

#### The Client Institution’s functions and responsibilities

#### The Project Director’s functions and responsibilities

#### The Coordination and Planning Team’s functions and responsibilities

#### The Project Execution Team’s functions and responsibilities

#### Participating consultancy firms and other participating firms’ functions and responsibilities

#### The functions and responsibilities of the Review Team

#### Work Plan

#### Procedures for assessing the professional candidates to the Execution Team

#### Completion schedules for the preliminary risk assessments and other studies, and for designing the facility

#### Overall budget for the assessments, design, and construction of the facility

#### Definition of communication channels and protocols

#### Between the specialists and the Institution, Project Director, and Coordination Team

#### Among and within the various specialist teams

#### Schedule of coordination meetings with representatives of the various specialist teams, the Institution, the Project Director, and the Coordination Team

#### Deadlines for the delivery and update of plans and specifications2

#### Definition of review, follow-up, and control mechanisms

#### Reviews by the Project Director or his or her staff

#### Reviews by the teams of specialists3

#### Reviews across disciplines4

#### External professional inspection

#### Definition of review mechanisms for the final project 5

#### General review regarding the fulfillment of design criteria

#### Review of calculation logs

#### Review of siting plans

#### Review of architectural plans

#### Plans of the various sections of the facility

#### Floor plans

#### Section and elevation plans

#### Architectural detailing and finishing plans

#### Other architectural components (doors, windows, stairs, appendages, signs, etc.)

#### Review of structural plans

#### General specification plans

#### Foundation plans

#### Floor plans

#### Section and elevation plans

#### Structural detailing

#### Review of layout plans for basic facilities, lifelines, clinical gases, A/C ducts, electrical wiring, etc.

#### Review of installation plans for equipment, furnishings and other components

#### Review of plans for details, connections and anchoring of components

#### Review of other plans

#### Review of tender documents

#### Review of technical specifications

#### Review of equipment installation specifications

#### Review of construction and procedures manual

#### Review of general contract conditions

#### Review of units of measures, quantities of materials and so on, completion schedule, construction budget and forms of payment

#### Review of other tender documents

#### Definition of inspection procedures during the construction process

#### Listing of construction procedures that require inspection or specialized inspection, and type of inspection required

#### Listing of components and services that require inspection or specialized inspection, and type of inspection required

#### Characteristics of the expected reports (See Table 29)

| Notes: | 1 | The selection of the participating design professionals, as well as the assignment of responsibilities, must be carried out with special care. Conflicts of interest tend to affect the quality of the project. |
| --- | --- | --- |
|  | 2 | Each discipline must work based on the most up-to-date information issued by the other disciplines in timely fashion. |
|  | 3 | Each plan, technical specification, or tender document must be checked by at least one expert from another discipline than that of the expert who produced it. |
|  | 4 | Multidisciplinary projects need to be checked at each stage by all the disciplines involved. |
|  | 5 | Before the final plans are issued, they must be submitted to the other disciplines for review and commentary. |

#### Project Quality Assurance: the Construction Stage of the Project

The following table specifies the minimum tasks that must be carried out in order to ensure the correct execution of the project in its construction stage.

#### Table 28 Quality Assurance Program for the Construction Stage of the Project

#### Conditions for the start of the construction

#### Final design plans approved

#### Technical specifications approved

#### Tender documents approved by the parties

#### Contract signed

#### Responsibilities of the Client Institution, Project Director and Coordination Team

#### Present the Contractor with a feasible project

#### Provide the necessary financing

#### Provide an adequate site

#### Choose the most suitable Technical Inspection Team

#### Participate in the decision-making process in matters critical to the project or unregulated issues

#### Report to the Specialists and to the Construction Firm, in timely fashion, any modifications to the project

#### Remain up to date on the progress and state of the construction

#### Meet any other responsibilities stipulated in the contract

#### Definition of the Equipment Designer’s functions during the construction stage

#### Report to the Institution, Project Director, and Coordination Team, in timely fashion, any changes to the original project

#### Assist the Technical Inspection Team in protection matters (a interpreter of the technical specifications)

#### Participate in the decision-making process concerning matters critical to the project, or unregulated matters that require attention

#### Evaluate protection options presented by the Construction Firm to the Technical Inspection Team

#### Carry out on-site specialized inspections

#### Issue certificates of approval of the works

#### Definition of Consultancy Firms and Suppliers (See Chapter V)

#### The General Contractor’s main functions

#### Manage the administrative and legal aspects of the intended construction

#### Review upon receipt the architectural, structural, equipment, and detail plans

#### Review upon receipt all technical specifications

#### Ensure that the construction meets all the plan and specification requirements and permits set by law.

#### Ask suppliers to provide all safety certificates required

#### Supervise the pace at which the construction advances

#### Control all resources used in the construction

#### Carry out any tests needed to ensure the quality of the project

#### Produce reports on the progress of the construction

#### Establish program of payments to Suppliers and Subcontractors

#### Keep the Construction Log up to date

#### Carry out any other tasks stipulated in the contract

#### Definition of the Construction Firm’s responsibilities

#### Be fully aware of the details and objectives of the project

#### Acquire materials, hire labor, and arrange subcontracts of a quality befitting the requirements of the project

#### Assume responsibility for the actions of all subcontractors

#### Assume responsibility for the construction methods and sequences

#### Update the Construction Log in timely fashion

#### Respond in timely fashion to the requirements of the Institution and Coordination Team, Technical Inspection Team, Specialists, and External Inspectors

#### Provide access to external inspections, inspections by the Project Director, by the Technical Inspection Team and the other disciplines in charge of the design of the construction1

#### Report to the Technical Inspection Team any modification, voluntary or involuntary, to the original project

#### Report to the Technical Inspection and Coordination Teams in timely fashion the results of any tests

#### Assume responsibility for on-site safety during the construction process

#### Carry out any other tasks called for in the contract

#### Definition of the Technical inspection Team (See Chapter V)

#### Definition of the Technical Inspection Team’s Functions

#### Control the implementation of the construction program based on the performance objective assigned.

#### Review the construction procedures

#### Regularly engage in inspections regarding the quality of the construction materials used

#### Verify the quality of the labor employed

#### Assist the General Contractor in specific technical matters

#### Supervise the work of the external inspectors

#### Verify compliance with project specifications

#### Participate in the decision-making process in matters critical to the project or unregulated issues

#### Act as a permanent liaison between the Contractor and the Institution, the Project Director, and the Coordination Team

#### Continually check the construction log

#### Safeguard and control contractual documents

#### Verify the application of the correct safety measures during the construction process

#### Carry out any other contractual obligations

#### Definition of external bodies in charge of inspections and tests2

#### Produce an inspections and tests program3

#### Requirements affecting external inspection and test groups

#### Operate independently of the building firm

#### Be fully aware of the details and objectives of the project

#### Be fully aware of the plans and specifications of the project

#### Be fully aware of the stages of the construction process

#### Continuously and effectively inspect the materials, equipment and procedures used in the construction4

#### Extract representative samples based on the methods and materials employed on the construction

#### Report to the Construction Firm and the Technical Inspection in timely fashion (See Table 29)

#### Carry out any other tasks called for in the contract

#### Definition of channels and protocols of communication of results of trials and tests

#### From the body in charge of inspections to the Construction Firm

#### From the Construction Firm to the Technical Inspection Team

#### From the Technical Inspection Team to the Design Team and the Institution

#### As-Built Report on the facility5

#### Listing of professionals and specialists that participated in the project

#### Reports on regional and local risk (if applicable)

#### Definitive calculation logs

#### Construction Log and related documents

#### Inspection Reports

#### Test results

#### Safety certificates for the components, and certification of correct construction practices

#### Listing of codes and standards that were applied

#### As-built plans of architectural components and furniture

#### As-built plans of the structural system

#### As-built plans of the mechanical and electrical systems and equipment

#### As-built plans of basic facilities, clinical gases, ducts, A/C, fire extinguishing network, etc.

#### Other As-built information as defined by the Institution and the Coordination Team

#### Definition of criteria for acceptance of the works

#### Effective conclusion of the works stipulated in the contract

#### Compliance with the specifications of the project

#### Approval of As-built Report

#### Satisfactory implementation of tests on the operation of services, systems and equipment

#### Fines paid

#### Return of deposits

#### Reception of the construction by fiscal bodies

#### Delivery of the construction to the institution

#### Signed minutes of final reception of the works

#### Other criteria stipulated in the contract

| Notes: | 1 | The Client Institution or the specialists that participated in the design stage may demand that the Construction Firm stop the works if the safety requirements and quality standards stipulated in the project documents are not being met. |
| --- | --- | --- |
|  | 2 | All equipment and tools used in the inspections, trials or tests must have certificates of calibration issued by a recognized institution. |
|  | 3 | The body in charge of the trials and tests must have permanent access to the construction site. |
|  | 4 | The body in charge of the trials and tests may reject the use of particular materials and equipment. |
|  | 5 | The As-Built Report must be produced for any building with a functional or investment protection objective. For buildings with a life-safety performance objective, the As-Built Report must be produced if is expressly requested by the Institution, the Project Director or the Coordination Team. |

The following table lists the key contents of the construction inspection report.

Table 29 Characteristics of Inspection Reports

Inspection or Test Report

General Information (date, hour, etc.)

Staff in charge of the inspection or test

Procedures employed during inspection or test

List of equipment used during the inspection or test

Certificate from body in charge of calibrating the equipment and tools used in the inspection process

Results of the inspection or test

Characteristics of the materials inspected or tested

Characteristics of construction processes inspected

Results of the tests of materials or tests of operation

Inspected activities carried out or completed in compliance with project plans and specifications

Aspects in which there is no compliance with the project plans, specifications, standards and/or codes

Report of Non-compliance

Description of the non-compliant feature (including text and/or sketch specifying how aspect does not comply with the plans, etc.).

Location of the non-compliant feature

Qualitative description of the non-compliant feature

Other characteristics of the non-compliant feature

Actions needed to correct non-compliance

Processes that must be modified in order to prevent the recurrence of non-compliance

Deadlines for correcting the problem

- References

Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000.

Building Officials Code Administrators International, International Building Code 2000.

Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001.

Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001.

Department of the Army, ER 5-1-11: U.S. Army Corps of Engineers Business Process, Management, Regulation, Washington, D.C., August 2001.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988.

European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998.

Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Evaluation of Existing Buildings, Washington, D.C., 1998.

Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000.

Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994.

International Standards Organization, ISO 12491:1997: Statistical Methods for Quality Control of Building Materials and Components.

International Standards Organization, ISO 13485:1996: Quality Systems, Medical Devices, Particular Requirements for the Application of ISO 9001.

International Standards Organization, ISO 13488:1996: Quality Systems, Medical Devices, Particular Requirements for the Application of ISO 9002.

International Standards Organization, ISO 9000:2000: Quality Management Systems, Fundamentals and Vocabulary.

International Standards Organization, ISO 9001:2000: Quality Management Systems, Requirements.

International Standards Organization, ISO 9002:1994: Quality Systems, Model for Quality Assurance in Production, Installation and Servicing.

International Standards Organization, ISO 9003:1994: Quality Systems, Model for Quality Assurance in Final Inspection and Test.

Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001.

Patrucco, H., and G. McGavin, Survey of Non Structural Damage to Healthcare Facilities in the January 17, 1994 Northridge Earthquake.

Sistema Nacional de Protección Civil, Centro Nacional de Prevención de Desastres (CENAPRED), Calidad en Diseño, Construcción y Supervisión de Obras: Comparación de la Práctica en México, Japón y EUA, Memoria del Taller, 23 – 27 de Agosto, Mexico, 1993.

U.S. Army Corps of Engineers, Engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998.

ANNEX A

STUDIES REQUIRED FOR 
CHARACTERIZING NATURAL HAZARDS

The scope of the various studies needed to characterize prevailing hazards depends in great measure on the local conditions of each region. However, by way of reference, the following tables list some of the details that must be taken into account when considering the various hazards considered in this handbook.

Table A.1 - Landslides

Table A.2 - Mudslides

Table A.3  - Strong winds and hurricanes

Table A.4  - Flood

Table A.5  - Earthquakes

Table A.6 - Volcanic activity

#### Table A.1 #### Collection of Background Data for the Assessment of Local Landslide Risk

Collection of data related to:

Topography of the region

Vegetable covering of the region

Overall characterization of the soils of the region

Topographical studies

Evidence of historical or recent landslides

Estimation of the volume and shape of unstable masses

Assessment of current landslide velocity

Geological studies

Assessment of soil degradation

Prevalent types of strata and sediments

Prevalent kinds of seismic faults and fractures

Geological characterization of the materials

Soil mechanics studies

Geomechanical characterization of the materials

Stratigraphic characterization

Execution of bores or soundings

Identification of stratigraphic sections

Identification of low resistance strata

Characterization of fault lines (interface with rock base)

Terrain tests

Site density

Extraction of unaltered samples (only if detailed assessment is required)1

Maximum and minimum densities

Determination of shear resistance parameters in drained and non- drained conditions

Geophysical studies (only as a complement to soil mechanics)1

Stratigraphic characterization

Geoseismic profile

Resistivity

Gravimetry

Characterization of seismic demand

See Regional Seismicity Study

#### Table A.2 #### Collection of Background Data for Assessment of Mudslide Risks

Collection of data related to:

Topography of the region

Vegetable covering of the region

Overall characterization of the soils of the region

Topographical studies

Identification of local morphological characteristics that influence the likelihood of mudslides

Characterization of vulnerable slopes

Height of the slope

Length of the slope

Steepness of the slopes

Identification of melting snow masses

Geological studies

Same as in assessment of landslide risk

Soil mechanics studies

Same as in assessment of local landslide risks, but must also carry out the following:

Geomechanical characterization of materials

Terrain tests

Measurement of soil permeability

Standard penetration test

Liquefaction potential assessment

Hydrology studies

Characterization of local runoff regimes

Meteorological studies

Pluviometry

Characterization of region’s pluviosity

Annual and monthly precipitation

Daily precipitation

Type of precipitation and location of snow lines

Spatial and temporal distribution of precipitation

Production of precipitation intensity-duration-frequency curves

# Other background data on the region

Overall characteristics of runoff surface

Inclination and length of vulnerable slopes

#### Table A.3 #### Collection of Background Data for Assessing the Risk of Strong Winds and Hurricanes

Collection of data related to:

Topography of the region

Vegetable covering of the region

Overall characterization of the soils of the region

Topographical studies

Characterization of local factors that influence the formation of turbulences

Meteorological studies

Wind intensity in the region

Measurement of wind speeds

Study of wind height distribution

# Other background data on the region

Characteristics of the buildings that surround the potential site

#### Table A.4 #### Collection of Background Data for Assessing the Risk of Flood

Collection of data related to:

Topography of the region

Vegetable covering of the region

Overall characterization of the soils in the region

Local Topographical Studies

Identification of low-lying areas in the sector

Characterization of the river basin

Surface of the basin

Length of the basin

Maximum, minimum and median slopes of the basin

Characterization of the watercourses

# Meteorological studies

Pluviometry

Characterization of region’s pluviosity

Annual and monthly precipitation

Daily precipitation

Type of precipitation and location of snow lines

Spatial and temporal distribution of precipitation

Production of precipitation intensity-duration-frequency curves

Fluviometry, hydraulics and hydrology studies

Estimation of water volume (fluviometry)

Study of historical river surges

Estimation of water volume in situ

Regional analysis of river surges

Synthetic unitary hydrogram

Rational method

Calculation of exceedance probabilities

Hydrological studies

Characterization of local runoff regimes

Hydraulic studies

Compilation of background data for calculating hydraulic axes

# Other background data on the region

Overall characteristics of surface runoffs

#### Table A.5 #### Collection of Background Data for Assessing Seismic Risk

Regional seismicity study

Study of historical seismicity in the region

Cataloging of seismic events in the region

Identification and characterization of the sources of seismic events

Local topographical studies

Identification of morphological characteristics

Local geological studies

Identification of geological faults1

Geomorphological characterization of the materials

Soil mechanics studies

Identification of freatic level

Stratigraphic characterization

Execution of bores, trenches and/or soundings

Geophysical methods (See specific point)1

Seismic characterization of the foundation soil

Terrain tests 1

Extraction of unaltered samples (only if detailed study is required)

Maximum and minimum densities

Drained and non-drained support capacity

Standard penetration test

Density in situ

Modified proctor

Laboratory tests

Maximum and minimum densities

Consolidation

Triaxial

Classification

Assessment of liquefaction potential

Geophysical studies1

Stratigraphic characterization and identification of freatic level

Wave propagation velocity: Cross hole and Down hole

Geoseismic profile

Electrical resistivity

Gravimetry

#### Table A.6 #### Collection of Background Data for Assessing the Risk of Regional Volcanic Activity

Collection of data related to:

Topography of the region

Overall characterization of the soils in the region

Topographical studies local

Identification of local morphological characteristics

Detection of historical evidence of eruptions

Identification of lava-flow paths

Volumes of water stored in craters

Existence of snow in the area (only if applicable)

Local geological studies

Characterization of volcanic activity in the region

Delimitation of the area at risk

Estimation of the magnitude and area of influence of possible events

Other background data on the region

Evidence of volcanic activity

| Notes: | 1 | These studies must be carried out only if detailed studies are required, as well as in special cases. |
| --- | --- | --- |

ANNEX B

ACCEPTED LEVELS OF DAMAGE

TO STRUCTURAL AND NON-STRUCTURAL COMPONENTS

(SEISMIC SCENARIO)

The following table, adapted from FEMA 356, specifies the damage levels that may be considered acceptable for a non-health facility subjected to a design earthquake, depending on two different performance objectives for the structural system. In the specific case of a health facility, it is advisable to set down in writing the acceptable damage levels for the two levels of risk described in this handbook. This level of acceptable damage must be approved by the Institution and the Coordination, Design and Review Teams. The following is for illustrative purposes only.

| Table B1 Acceptable Structural Damage for Two Levels of Protection |  |  |
| --- | --- | --- |
| Type of Component | Functional Component Protection (FCP) | Life-Safety Component Protection (LCP) |
| Reinforced concrete frame systems | Low level of cracking (unit deformations lower than 0.003). Creeping of beams and columns in very few sectors. No permanent deformations. | Considerable damage to beams and ties: loss of coverings and significant cracking Deformation of ductile elements. Limited cracking and failure of joints in non-ductile columns. Severe damage to short columns. Interstory deformations of up to 1 percent are acceptable. |
| Steel moment-resistant frame systems | Creeping of beams and columns in very few sectors. No fractures. No visible permanent local warping or deformation of the elements. | Local warping of some beams and severe distortion of ties may take place. Failure of some of the moment connections. The shear connections remain intact. A few elements may suffer partial failure. Interstory deformations of up to 1 percent acceptable. |
| Braced steel frame systems | Low level of creeping and warping of bracing systems. No visible permanent brace deformations. | The bracing system may suffer deformation and display warping. The failure of these elements is not acceptable. Connection failure is acceptable. |
| Reinforced concrete wall systems | Only a low level of cracking in walls (width of cracks of less than 1.6 mm) is acceptable. Beam couplings may suffer cracking (width of cracks of less than 3.2 mm). | Damage to wall edging elements is acceptable, as is damage around openings, some detachment of coverings, and cracks due to bending. Significant cracking due to bending and shearing in beam couplings is acceptable. |
| Reinforced masonry wall systems | Cracks of less than 3.2 mm in width are acceptable. Leaking or displacements beyond the plan are not acceptable. Permanent interstory deformations of up to 0.2 percent are acceptable. | Generalized cracking of walls (width of crack of less than 6.4 mm) is acceptable. So is the damage around wall apertures and corners the failure of some units. Permanent interstory deformations of up to 0.6 percent are acceptable. |
| Confined masonry wall systems | Minor cracking in the masonry panels is acceptable (width of cracks of less than 3.2 mm). Minor damage to veneers and coverings is acceptable. Permanent interstory deformations are not acceptable. | A high level of damage to the masonry panels is acceptable. However, neither the leaking of the panels nor the fall of coverings is acceptable. Permanent interstory deformations of up to 0.3 percent are acceptable t |
| Wood paneling wall systems | Minor cracks in the plaster and coverings are acceptable. Permanent interstory deformations of up to 0.25 percent are acceptable. | Moderate damage to the joints and panels is acceptable. Permanent interstory deformations of up to 1.0 percent are acceptable. |
| Prefabricated system joints | Damage to the joints is not acceptable. Minor damage (width of cracks of less than 1.6 mm) is acceptable in the joints area. | Local damage in the area of joints is acceptable, but not the failure of the joints, nor is the dislocation of elements. |
| Foundations | A low level of settlements and uplifting is acceptable. | A total settlement of less than 15 cm, and a differential settlement of less than 4cm/m, is acceptable. |
| Metal diaphragms | The connections between the units and the connections to the support elements must remain intact. A low level of panel distortion is acceptable. | Damage to isolated welding is acceptable, as is local warping along some specific points of the panels. |
| Wood diaphragms | The joints must not show damage of any type. | Light cracking around some connections is acceptable. |
| Reinforced concrete diaphragms | Cracks of a width of less than 3.2 mm are acceptable. | Generalized cracking (width of cracks of less than 6.4 mm) is acceptable. So is localized damage. |
| Prefabricated diaphragms | Only a low level of cracking, localized in the joints, is acceptable. | Generalized cracking (width of cracks of less than 6.4 mm) is acceptable. So is localized damage. |

| Table B2 Acceptable Damage to Architectural Components for Two Levels of Protection |  |  |
| --- | --- | --- |
| Type of Component | Functional Component Protection (FCP) | Life-Safety Component Protection (LCP) |
| Chimneys | Negligible damage. | General damage. No collapse. |
| Suspended ceilings | Damage generally imperceptible. Slight dislocations in isolated hanging panels. Some cracks in rigid ceilings. | General damage. Some suspended ceiling modular panels may fall. Moderate cracks in hard ceilings may occur. |
| Stairs | Negligible damage. | Some cracks. The element remains operational. |
| Façades, parapets and curtain walls | Minor damage. | General damage. Collapse is allowed in sectors where people cannot be present. |
| Marquees | Minor damage. | Moderate damage. |
| Interior partitions | Cracks (width of less than 1.6 mm) around openings and corners. | General damage. Some severe cracks. |
| Doors | Minor damage. Doors remain operational. | General damage to doors. Some doors will get stuck. |
| Glass surfaces | Some glass surfaces cracked. None breaks. | Generalized cracking. Small fractures of glass surfaces. |
| Office furniture (shelves, cabinets, desk equipment, etc.) | Desk equipment remains in place and operational. Some filing cabinets may slide and open, but do not tilt or spill their contents. | Some equipment falls off the desks. Some light-weight filing cabinets may overturn, so long as they pose no risk during evacuation. |
| Computers and communication systems | The systems do not suffer damage and remain operational. | Cables may be disconnected. The equipment may slide, but not overturn. |
| Manufactured equipment in general1 | The equipment remains safe and operational. | The equipment slides but does not fall over. Some equipment may need repair. No risk for patients or employees. The equipment that provides critical services remains in operation. The equipment with dangerous or harmful contents does not suffer damage. |
| Medical equipment in general | The equipment remains safe and operational. | The equipment slides but does not fall over. Some equipment may need repair. No risk for patients or employees. The equipment that provides critical services remains in operation. The equipment with dangerous or harmful contents does not suffer damage. |
| HVAC equipment | Units remain safe and operational. | Units uncouple themselves from their supports. Ruptures occur, but no collapse, of ducts or piping, or direct joints to the equipment. |
| Clinical gases | Systems remain in operation. | Systems remain in operation. |
| Generators | The equipment remains operational. | Damage to supports. Some equipment may not function. The equipment that provides critical services remains fully operational. |
| Emergency lighting | System remains in operation. | Some lighting fixtures may be loosened. |
| Fire safety system | Damage negligible. Systems remain safe and operational. | Some sprinklers may be damaged by impact with suspended ceilings. Some leaking may occur. |
| Drinking water and sewerage systems | Systems remain in operation. | Some attachment and bracing systems may suffer damage. |
| Fire alarm systems | System remains in operation. | Sensors mounted on suspended ceilings may be damaged. Some may be out of order. |
| Duct systems | Damage negligible. The systems remain safe and operational. | Ducts may be loosened from their connections to equipment and outlets. Some supports may fail. |
| Lighting fixtures | Damage negligible. | Some lighting fixtures may break and fall off. Some light-weight fixtures may fall except in critical service areas. |
| Vertical transport systems | Vertical transport systems remain operational. | Vertical transport systems may fail, but counterweights will not be derailed. |
| General piping systems | Damage negligible. The systems remain safe and operational. | Minor damage to joints. Some leaks, easy to repair. Certain suspension and bracing components may be damaged but the systems remains suspended and stable. |

| Notes: | 1 | Includes industrial, mechanical, electrical, kitchen, and laundry equipment. |
| --- | --- | --- |

ANNEX C

COMPLEMENT TO

TERMS OF REFERENCE

FOR THE REDUCTION OF VULNERABILITY

IN THE DESIGN OF NEW HOSPITALS

COMPLEMENT TO

Terms of Reference for Vulnerability Reduction in the Design of New Hospitals

The following text is included for illustrative purposes only, and is solely meant to provide suggestions for enhancing the vulnerability reduction of health facilities through the inclusion of the recommended provisions in the traditional Terms of Reference for the design of a hospital or other kind of health facility.

- General issues

  - The present Terms of Reference are an integral part of the call to tender for the design of __________________ Hospital, and stipulate the additional requirements that must be met in the design of the hospital components’ protection systems to ensure that they meet the performance objectives defined for the facility in both normal and emergency conditions. The performance objectives for this hospital are presented in Table xx.

  - These provisions set minimum requirements only. Each consultant, specialist or supplier must establish and identify additional conditions that its design or product must meet in order to satisfy the protection performance objectives set by the Institution.

  - Quality assurance principles and means applied in this project will be recorded in a single document. No tacit agreements or implicit demands will be tolerated.

- Definition of the performance objectives

  - The facility and its services must withstand the following hazards: landslides, mudslides, strong winds and hurricanes, floods, earthquakes, and volcanic activity. For each hazard, two levels of intensity are specified. For each hazard and level of intensity, the Institution has defined the following performance objectives for the intended services.

| EVENT | Minimum level recommended ( Percentage/Years) | Performance objective (LS/IP/FP) | Maximum credible level desired ( Percentage/Years) | Protection objective (LS/IP/FP) |
| --- | --- | --- | --- | --- |
| Landslide |  |  |  |  |
| Mudslide |  |  |  |  |
| Flood |  |  |  |  |
| Earthquake |  |  |  |  |
| Strong winds |  |  |  |  |
| Volcanic activity |  |  |  |  |

  - The standby capacity (i.e., the capacity to remain isolated from critical utilities and services external to the hospital) is shown in the following table:

| Service | Standby Capacity |
| --- | --- |
| Drinking water | # hours |
| Electricity | # hours |
| Oxygen | # dies |
| Oil | # dies |

  - The stipulated times for the recovery of functional capacity in the case of each service are presented in Table xx (e.g., Table 14).

  - The hazard characterization documents, design procedures specific to each one of the hazards, and geotechnical properties of the proposed site, as specified below, are an integral part of this tender. (All relevant tender documents should be listed here).

- General design of the hospital

  - The design procedures must meet ISO9000 quality standards.

  - The person in charge of each team of specialists must have had at least 10 years’ experience in hospital infrastructure design relevant to the job he or she is intended to perform. In addition, his or her participation in the design of hospitals with a total built surface larger than 100,000 m2, and with at least one hospital built with a surface larger than 10,000 m2 during the same period, must be documented and certified.

  - The candidates to the various professional teams must present documents that certify their participation in the design of hospitals that have met investment protection and functional protection standards.

  - The documents produced during the design process, including specific protection considerations, should include the following:

- Calculation logs.

- Certificates that the performance objectives defined by the Institution have been met.

- Mockups.

- Siting plans.

- Architectural plans: general distribution plans, floor plans, section and elevation plans, architectural detailing plans and any other relevant plans.

- Structural plans, including general specification plans, foundation plans (based on the information provided by the soil mechanics specialists), floor, section and elevation plans, structural detailing plans, etc.

- Plans displaying the layout of basic facilities, lifelines, clinical gases, air conditioning, electrical distribution, etc.

- Industrial, mechanical, and electrical equipment floor plans.

- Furniture floor plans.

- Technical specifications.

- Specifications for equipment installation.

- Construction and building procedures manual.

- General conditions contained in the contract.

- Construction Program: units of measure, quantities, completion schedule, budget, and forms of payment, et alia.

- Terms of reference and other tender documents.

  - The documents listed above shall be easily understandable and clear enough to prevent errors of interpretation.

  - The systems used for component protection shall be feasible to build and amenable to effective maintenance.

  - Each team of specialists must prepare a document setting out clearly how it will meet the facility’s performance objectives and, particularly, what their requirements and restrictions are in relation to the other disciplines. Such documents must define, moreover, the criteria for analysis and design, and the codes of reference employed. They must be produced at the start of the project, and approved by the Client Institution.

  - The Project Director and Coordination Team will supervise the correct integration of the various construction efforts by the participating teams, including the architecture, structural calculation, and installation teams.  In order to do this, they shall coordinate all the specialist teams.  For this purpose, all the specialist teams will receive from the Director and Coordination Team specific coordination plans setting out in detail the layout of all the systems, equipment and components of the facility. These plans will superimpose the subprojects developed by all the disciplines and specify the layout and the points at which installations will meet, as well as the location of the various components, suspended ceilings, lighting fixtures, outlets, sanitary devices, HVAC devices, built-in furnishings, industrial equipment, medical equipment, and fire safety systems. Likewise, they will specify the layout of all the wiring, piping and ducts and their passage through walls, beams, foundations, columns, etc. These plans must be studied in detail by the Coordination Team and the specialist teams in order to ensure that the protection systems will work.

  - Before the final plans are issued, drafts must be delivered to the other disciplines for review and commentary.

- The design of the structure

  - The structural system chosen for the facility must meet the performance objectives set for the hospital and its services.

  - The team of structural engineering specialists will be in charge of ensuring the safety of the structure. When the performance objective of the facility and of its services is functional and investment protection, the team must provide a structural system that not only safeguards the structure but also the non-structural elements. Put differently, the structure must not only protect itself, but must make it possible to carry out the procedures required for the protection of the non-structural systems. For this reason, the structural system needs to be explicitly approved by all the participating disciplines.

  - The structural team must design their subproject in coordination with the architectural and other teams (sanitary, air conditioning, electrical, etc.) so as to meet their protection requirements, including perforations, anchoring, etc.

  - The structural system and its components must be designed to withstand permanent and eventual demands on the structure, including its dead load, live load, seismic and wind loads, snow and ash loads, temperature changes, hydrostatic and hydrodynamic thrust forces, total and relative foundation settlements, etc.

  - The structural design must incorporate such detailing as will ensure, for each level of risk, that the performance objective will be met.  It is important to include in the design any systems needed for guaranteeing that, in the event of damage and functional loss, services can be restored within a predefined timeframe.

  - The structural team must provide the information required by the other disciplines for the design of the equipment, systems, and other non-structural components.

  - The structural team must certify that the performance objective set by the Institution for the facility has been met.

- Design of non-structural components

  - The non-structural components must enjoy a level of protection that meets the performance objective set for the medical or support services to which they belong or to which they are directly or indirectly linked.

  - Each specialist team will be responsible for the design of the protection systems required by the components of their competence, and for certifying the fulfillment of the performance objective set by the Institution.

  - All the non-structural components to be protected must be adequately supported. The points of support of these elements must enjoy a level of safety comparable to that of the element itself.

  - In those cases in which the non-structural components exert pressures or lean on other non-structural components, the joint stability of all of them must be guaranteed.

  - The safety of any equipment containing hazardous materials must be clearly demonstrated.

  - The safety of the non-structural components may be assessed through analysis or the supplier or manufacturer’s certificate of safety.

  - If the safety assessment of the non-structural systems, equipment, and components is carried out through an analysis by the relevant team, they must present a calculation log recording, at a minimum, and as needed, the type of system, equipment or component, a description of the component, the performance objective considered in the design of the protection systems, the standards applied in the analysis, a description of the structure where the component is located, the behavior that determines the response of the component, characteristics of the component when in operation, characteristics of the component’s bracing, anchoring and support systems, the method of analysis, the demand considered, the results obtained, and an assessment of the component’s interaction with other systems, equipment or components.

  - If the safety assessment of standard non-structural systems, equipment, and components is based on the supplier or manufacturer’s certification through in-house analysis, that supplier or manufacturer must present a calculation log with the same contents described in provision 5.8.

  - If the safety assessment of standard non-structural systems, equipment, and components is based on the supplier or manufacturer’s certification through experimental means, the supplier or manufacturer must present a document with the following information: identification of the laboratory, standards of reference considered in the tests, description of the testing procedures, and test results.

  - In addition to the certificates described in provisions 5.8, 5.9 and 5.10, the following information should be provided: requirements for meeting the certification conditions (conditions of use, operation, installation, etc.), date of certification and validity of the certification, certification of compliance with the standards specified in the contract, and description of the applicability and limitations of the certificates.

Adapted from Noji, E., Impact of Disasters on Public Health, Pan American Health Organization (PAHO), 2000.

ECLAC/IDB, A Matter of Development: How to Reduce Vulnerability in the Face of Natural Disasters, prepared for the “Confronting Natural disasters: A Matter of Development” Seminar, by Ricardo Zapata M. and Rómulo Caballeros, 2000.

World Health Organization (WHO), Public Health in the Americas: New Concepts, Performance Analysis and Bases for Action, Scientific and Technical Publication Nº 589, 2002.

Principles of Natural Disaster Mitigation in Health Facilities (Pan American Health Organization, 2000), Disaster Mitigation for Health Facilities: Guidelines for Vulnerability Appraisal and Reduction in the Caribbean (PAHO, 2000), and FEMA 55: Coastal Construction Manual (Federal Emergency Management Agency, 1996) list the basic requirements for each hazard.

Cif. PAHO/WHO Collaborating Center on Disaster Mitigation in Health Facilities, Bases Metodológicas: Evaluación de Vulnerabilidad Sísmica de Edificaciones Estructuradas con Pórticos de Concreto Preformado, Evaluación de Elementos Arquitectónicos y Evaluación de Equipamiento, Universidad de Chile, 2000

I.e., they must be specified according to Form 1.A, or its equivalent, in the case of each likely hazard.