GUIDELINES FOR VULNERABILITY REDUCTION 
IN THE DESIGN OF NEW HEALTH FACILITIES

Rubén Boroschek Krauskopf, Ph.D.

Rodrigo Retamales Saavedra

PAHO/WHO Collaborating Center

Disaster Mitigation in Health Facilities

University of Chile

Pan American Health Organization

World Bank

ProVention Consortium

February 2003

Preface

Nowadays, when severe natural phenomena occur, health facilities generally experience temporary or permanent interruption of their services, damage to their infrastructure, and the partial or total loss of the considerable investment made in building and furnishing them—all of which has a significant negative impact on the social and economic development of the country and its inhabitants. Such situations arise because all too often, in the design of such facilities, the sole objective regarding the performance of the building in disaster situations has been protecting the lives of the staff and users. While this is an indispensable goal, and one that has been met with a certain degree of success, the consequence of such a limited vision has been, in practice, the building of facilities that offer little or no protection to the investment made or to their crucial function within the health system.

Historically, to make matters worse, the choice of where the facilities were to be located has often been made with little awareness of the natural hazards present in the area and their likely effects on structures, operations, and the surrounding community. Finally, it is by no means rare to find construction or maintenance practices that curtail or even neutralize altogether the few safety measures that were incorporated in the design of the facility.

A turnaround is needed.  While improving the safety of existing infrastructure is difficult and relatively costly, the incorporation of investment and functional protection in the design and construction of new facilities is simple and comparatively inexpensive. The value of applying such criteria has already been proven in such disasters as the earthquakes that hit Northridge (Los Angeles) in the United States in 1994 and Kobe in Japan in 1995, where hospitals and other important facilities within the epicenter area managed to remain in operation.

Such an approach, however, requires an awareness of the facility’s desirable level of performance in the face of different disaster scenarios of varying intensity. The objective can be life safety, investment protection, or functional protection. To reach the chosen objective it is necessary to reorganize the way in which new health facilities have traditionally been conceived and buil. What is needed is the use of designs and construction methods that take into account the natural hazards likely to affect the site and the surrounding region, as well as the performance objective desired. International experience shows that basing a new project on such a philosophy only increases total costs by less than 4 percent. This is a fraction of the direct losses the sector suffers annually as a result of insufficient disaster preparedness—not to mention the social, political, and economic impact of the breakdown in services, or the total loss of a costly and much needed hospital, laboratory, or blood bank, in the midst of a major emergency.

This handbook is aimed at health sector administrators, professionals, and consultants whose task is the management, design, construction, and inspection of new health facilities. It specifies the activities that must be carried out throughout all relevant stages, including preliminary planning, the selection of the team of professionals that will participate in the project, the choice of site, and the design and construction of the project itself.

PAHO/WHO Collaborating Center for

Disaster Mitigation in Health facilities

University of Chile

Chapter I

Natural Phenomena and Health Infrastructure

- Introduction

Major natural disasters in the last two decades have affected at least 800 million people.  They have caused thousands of deaths, as well as economic losses of more than 50 billion U.S. dollars. Growing population density in several regions of the planet—and the consequent settlement of high-risk areas—are likely to make matters worse. Between 1981 and 2001, according to the Pan American Health Organization, more than 100 hospitals and 650 health units in the hemisphere were severely damaged by the action of natural phenomena, causing direct economic losses of close to 3.1 billion dollars.

Tables 1 through 3 show some of the effects of adverse natural phenomena on health infrastructure.

| Table 1 Effects of Hurricanes On Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Nature of the Phenomenon | Overall Effects |
| Jamaica, Hurricane Gilbert | 1988 | Category 5 | 24 hospitals and health centers damaged or destroyed. 5,085 patient beds lost. |
| Costa Rica and Nicaragua, Hurricane Joan | 1988 | Category 4 | 4 hospitals and health centers damaged or destroyed. |
| Dominican Republic, Hurricane Georges | 1998 | Category 3 | 87 hospitals and health centers damaged or destroyed. |
| Saint Kitts-Nevis, Hurricane Georges | 1998 | Category 3 | Joseph N. France Hospital in Saint Kitts suffered severe damage. 170 beds lost. |
| Honduras, Hurricane Mitch | 1998 | Category 5 | 78 hospitals and health centers damaged or destroyed. Honduras’ national health network severely affected, rendered inoperative just as over 100,000 people needed urgent medical attention. |
| Nicaragua, Hurricane Mitch | 1998 | Category 5 | 108 hospitals and health centers damaged or destroyed. |

| Sources | : | Based on Natural Disasters: Protecting the Public Health, Scientific Publication Nº575, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |

| Table 2 Effects of Floods on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Nature of the Phenomenon | Overall Effects |
| Pacific and Andean Region of South America | 1997-1998 | Floods associated with the El Niño Phenomenon | The floods placed grueling demands on the health system to combat acute respiratory infections, acute diarrheic diseases, vector-borne diseases (malaria, classic dengue, hemorrhagic dengue, yellow fever, encephalitis, Chagas disease, etc.), water- and food borne diseases (cholera, salmonellosis, typhoid fever, viral hepatitis, multiple intestinal parasitism, etc.) and skin diseases (scabies, bacterial infections and mycoses, etc.). |
| Ecuador | 1997 | Floods associated with the El Niño Phenomenon | Chone Hospital, not yet inaugurated at the time of the flood, suffered severe losses in medical equipment, furnishings, supplies and drugs. |
| Venezuela | 1999 | Torrential rains affecting states along the Eastern, Central and Western coasts of the country | The floods affected 31 hospitals and 687 outpatient clinics. |

| Sources | : | Crónicas de Desastres Nº 8: Fenómeno El Niño 1997-1998, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |

| Table 3 Effects of Earthquakes on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Event & Location | Date | Magnitude | Overall Effects |
| San Fernando, California | 1971 | 6.4 | Three hospitals suffered severe damage and were unable to operate normally at the very moment they were most needed. Worse still, most of the disaster-related deaths and injuries occurred in the two hospitals that collapsed. Olive View Hospital, one of the most severely affected, had to be demolished and rebuilt. Since this was done in the traditional fashion, however, the new facilities suffered severe non-structural damage in the earthquake of 1994, putting them out of service. |
| Managua, Nicaragua | 1972 | 5.6 | The General Hospital was severely damaged. It had to be evacuated and, subsequently, demolished. |
| Guatemala City, Guatemala | 1976 | 7.5 | Several hospitals required evacuation. |
| Popayán, Colombia | 1983 | 5.5 | Damage and interruption of services at the San José University Hospital. |
| Chile | 1985 | 7.8 | 79 hospitals and health centers damaged or destroyed. 3,271 beds lost. |
| Mendoza, Argentina | 1985 | 6.2 | Over 10 percent of the total hospital beds in the city were lost. Of the 10 facilities affected, one had to be evacuated; two were subsequently demolished. |

| Table 3 (Continued) Effects of Earthquakes on Health Systems |  |  |  |
| --- | --- | --- | --- |
| Identity Event | Date | Magnitude | Overall effects |
| Mexico City, Mexico | 1985 | 8.1 | Structural collapse of five hospital facilities and major damage to another 22. At least 11 facilities had to be evacuated. Direct losses were estimated at US$ 640 million. The hospitals that suffered the most were the National Medical Center of the Mexican Social Security Institute (IMSS), the General Hospital, and Benito Juárez Hospital. Between the patient beds destroyed and those taken out of service due to evacuation, the seismic event caused a sudden deficit of 5,829 beds. At the General Hospital, 295 died; at the Juárez, 561. Among the casualties: patients, doctors, nurses, administrative staff, visitors, and newborns. |
| San Salvador, El Salvador | 1986 | 5.4 | 2,000 beds lost. Over 11 hospital facilities affected: 10 had to be evacuated, one condemned. Total damage was estimated at US$ 97 million. |
| Tena, Ecuador | 1995 | 6.2 | Velasco Ibarra Hospital (120 beds) suffered moderate non-structural damage—cracking on several walls, breaking of glass windows, collapse of ceilings, elevator system failure, and damage to water and oxygen pipes—forcing evacuation of the facilities. |
| Aiquile, Bolivia | 1998 | 6.8 | Carmen López Hospital severely damaged. |
| Armenia, Colombia | 1999 | 5.8 | 61 health facilities damaged. |
| El Salvador | 2001 | 7.6 | 1,917 hospital beds--39.1 percent of the country’s total capacity--lost. Severely damaged San Rafael Hospital was able to continue providing partial services—outdoors, on the hospital grounds. Rosales Hospital lost its capacity to provide surgical services as a result of the damage to several key wings. San Juan of Dios (San Miguel) and San Pedro (Usulután) Hospitals suffered considerable damage, and were only able to continue providing partial services outdoors, on their grounds. The Oncology Hospital had to be completely evacuated. |

| Sources | : | Based on Principles for Natural Disaster Mitigation in Health Facilities, Pan American Health Organization, 2000. |
| --- | --- | --- |
|  |  | Based on Natural Disasters: Protecting the Public Health, Scientific Publication Nº575, Pan American Health Organization, 2000. |
|  |  | Health in The Americas, 2002 Edition, Volume I, Pan American Health Organization, 2002. |
|  |  | Daños Observados en los Hospitales de la Red de Salud Asistencial de El Salvador en el terremoto del 13 de Enero de 2001, Informe Preliminar, Boroschek, K. y R. Retamales, 2001. |

Adverse natural phenomena affect health systems’ operations in two ways:

- Directly, by

  - Damaging healthcare facilities.

  - Damaging the infrastructure of the region, leading to the breakdown of public services indispensable to health facility operations as well as the destruction of access roads.

- Indirectly, by

  - Causing an unexpected number of deaths, injuries, or disease outbreaks in the affected community, exceeding the capacity of the local healthcare network.

  - Prompting spontaneous or organized migrations away from the affected area towards other areas whose health systems’ capacity may be overwhelmed by the new arrivals.

  - Increasing the potential risk of a critical outbreak of communicable or psychological diseases among the affected population.

  - Causing food shortages that lead to malnutrition and undermine resistance to various diseases.

Table 4 lists the most common effects of the natural hazards considered in this handbook:

|  | Table 4 Likely Effects of Various Natural Hazards |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Effect | Earthquakes | Strong Winds | Tsunamis and Flash floods | Ordinary Floods | Landslides | Volcanic and Lahar Activity |
| Loss of lives | High | Low | High | Low | High | High |
| Severe injuries requiring complex treatment | High | Moderate | Low | Low | Low | Low |
| Major risk of communicable diseases | Potential risk following all significant phenomena (Likelihood increases with crowding and the degradation of sanitary conditions) |  |  |  |  |  |
| Damage to health facilities | Severe (structure and equipment) | Severe | Severe but localized | Severe (equipment only) | Severe but localized | Severe (structure and equipment) |
| Damage to water supply systems | Severe | Light | Severe | Light | Severe but localized | Severe |
| Food scarcity | Infrequent (generally caused by economic or logistical factors) |  | Common | Common | Infrequent | Infrequent |
| Large migrations | Infrequent (common in severely affected urban areas) |  | Common (Generally limited) |  |  |  |

| Source | : | Vigilancia Epidemiológica Sanitaria en Situaciones de Desastre, guía para el nivel local, Pan American Health Organization, 2002. |
| --- | --- | --- |

The interruption of a health facility’s operations after a disaster may be short-term (hours or days), or long-term (months and years). It all depends on the magnitude of the event and its effects on the sector. Magnitude cannot be controlled; its consequences, however, can be.

When it comes to a future health facility, the effects of these phenomena can be controlled if site selection is guided by sound information and criteria, and the design, construction, and maintenance can withstand local hazards. For instance, Concepción’s Main Hospital in the south of Chile managed to continue operating in spite of being near the epicenter of the country’s most devastating earthquake of the 20th Century, which took place on 21-22 May 1960.

Failures are, by and large, more widely publicized than successes—but the Concepción case is by no means exceptional. Another example worth noting is the vastly different behavior of two hospitals, located right next to each other, that were hit by the Northridge earthquake of 1994. The first, USC Medical Center Hospital, had been designed employing a seismic protection system called base isolation. Not only did it suffer no structural damage, but none of its equipment or key contents was overturned in the quake, and the facility remained in operation throughout the crisis and beyond.  The other, adjacent facility had been designed and built according to traditional standards.  Its damage was so severe it could not continue to operate, and it was eventually demolished.

- Economic aspects

Several reports by the United Nations Economic Commission for Latin America and the Caribbean (ECLAC) has published state unequivocally that natural disasters are a significant obstacle to the economic and social development of the countries in the region. While adverse natural phenomena do not discriminate between industrialized and developing countries, their consequences can be very different. In 1998, for instance, 95 percent of the deaths associated with natural disasters took place in developing countries. There, adverse natural phenomena are far more likely to devastate the population’s standard of living and their development prospects. By contrast, natural phenomena generally affect only marginally the economy and population of developed countries.  (See Table 5).

| Table 5 Effect of Natural Disasters On National Economies |  |  |  |
| --- | --- | --- | --- |
| Location | Event | Date | Effect on the Economy |
| Managua, Nicaragua | Earthquake, 7.2 on the Richter scale | 1972 | Fall of 15 percent in GDP and 46 percent in Managua’s industrial and productive activity. |
| Mexico | Earthquake, 8.1 on the Richter scale | 1985 | GDP fell by 2.7 percent |
| Nicaragua | Hurricane Joan | 1988 | GDP suffered an additional 2 percent reduction, 17 percent in the agricultural sector. |
| Ecuador | Floods caused by the El Niño Phenomenon | 1997-1998 | GDP growth 1.2 percent lower than expected in 1998. |
| Dominican Republic | Hurricane Georges | 1998 | GDP reduction of 1 percent compared to annual forecast. |
| Nicaragua | Hurricane Mitch | 1998 | GDP growth of 4 percent, 1.1 points lower than forecast for that year. |
| Honduras | Hurricane Mitch | 1998 | Fall in GDP of 7.5 percent. |

| Source: | ECLAC/IDB, A Matter of Development: How to Reduce Vulnerability in the Face of Natural Disasters, prepared for the “Confronting Natural disasters: A Matter of Development” Seminar, 2000 |
| --- | --- |

The effects of a natural disaster are amplified in the health sector, for several reasons: first, it is one of the sectors that tend to suffer important economic losses in such situations, given the significant investments required; second, its recovery also implies large outlays, difficult to procure at a time when the rest of the country is also trying to recover; and third, it needs to quickly recover its capacity, not only to continue meeting the normal demand for its services, but also to care for the population directly affected by the event.

- Disaster vulnerability reduction in health facilities

In recent years, after hurricane Mitch and the major El Salvador earthquakes, several countries, among them Argentina, Bolivia, Chile, Colombia, Costa Rica, Honduras and Peru, and international institutions such as PAHO/WHO, ECLAC, the Inter-American Development Bank (IDB) and the World Bank, have begun to raise awareness concerning the need to promote strategies for mitigating the vulnerability and managing the risks facing health systems in the region. Considerable progress has been made in the field of disaster education in medicine and nursing faculties, in schools of architecture and engineering. The lessons learned reveal that most of the losses in health infrastructure were due to location in vulnerable areas, inadequate design, or the lack of proper maintenance. While most efforts have focused on assessing and reducing the vulnerability of existing health facilities, in recent years a new and encouraging trend has taken hold: investing in new infrastructure based on investment or functional protection criteria. In Chile, for instance, starting in 1999, it is mandatory for project consultancy groups to include specialists in hospital vulnerability, whose role it is to ensure that performance criteria are incorporated into the design and construction of new health infrastructure.

The Pan American Health Organization, through its Public Health in the Americas initiative, has defined a set of Essential Public Health Functions (EPHF). Aimed at the health authorities of the region at all levels—central, intermediate, and local—they set the foundation for evaluating the current healthcare situation, improving public health practices, and strengthening the leadership of sanitary authorities. Among the essential functions agreed upon in June 2000, during the 126th session of PAHO’s Executive Committee, is reducing the impact of emergencies and disasters on health, which is to be achieved through the following actions:

- The planning and execution of public health policies and activities regarding prevention, mitigation, preparedness, response, and early rehabilitation.

- A multiple focus that addresses the threats and etiology of all possible emergencies or disasters that can affect a country.

- Participation of the entire health system, and the broadest possible intersectoral cooperation, in reducing the impact of emergencies and disasters on healthcare.

- The promotion of intersectoral and international cooperation in finding solutions to the health problems caused by emergencies and disasters.

- Objectives and scope of this handbook

The experience of several countries revelas that is possible to employ a methodology for the design and construction of new health facilities that is capable not only of ensuring the safety of human lives, as has been the case, but also of ensuring the safety of the investment in the facility and its continued operation as well. Depending on the characteristics of the health network and the economic resources available, it is strategically possible to build health facilities that enjoy a high level of functional and investment protection.  While no one can demand that such facilities remain perfectly intact and fully functional both during and immediately after a severe emergency, it is reasonable to expect them to recover in a reasonably short time, and at a reasonable cost.  Finally, if resources are limited or the natural or technical conditions do not allow it, health facilities can still be built that, confronted with severe natural phenomena, can suffer moderate or even considerable damage without imperiling the lives of their occupants—much as is the case now.

In order to meet the new and more ambitious performance objectives, it is necessary to establish new design and construction criteria—and engage in quality assurance from start to finish. Experience shows that the financial cost of applying these measures represents less than 4 percent of the total construction cost, and in some cases is practically zero since it only implies choosing a different location or changing the underlying design philosophy. In any case, the amount is marginal when compared to the economic costs of retrofitting or rehabilitating a structure damaged by a natural disaster—not to mention the social, political and economic impact of the temporary or permanent loss of a health facility.

The traditional stages in the project development cycle for the construction of new health facilities are the following:

Preinvestment:

Stage I: Identity of the need for a new health facility. At this stage, consideration is made of variables such as the characteristics of the existing healthcare network, current development policies, the rate of utilization of existing services, expected demand, epidemiological and demographic profiles, health policies, and geographical characteristics of the area. Directly associated with this stage is the search for financing for the development of the new facility.

Stage II: Assessment of options to meet this need. At this stage the various options for meeting the need for a new health facility are identified, assessed, and compared. The definitive location of the facility is an essential variable in this process.

Stage III: Medical architectural program and preliminary plans. In this stage the services and spaces desired are defined and preliminary plans are drafted in order to determine the functional relations and basic characteristics of the new infrastructure.

Investment:

Stage IV: Project design. In this stage the project plans, specifications, budget, and tender documents are drawn up.

Stage V: Construction. At this stage, the new infrastructure comes into physical existence.

Operations:

Stage VI: Operations and maintenance. While this stage is not part of the development of the new infrastructure, it is indispensable that in the previous stages the way the facility will operate and remain functional is defined in advance.

The chief purpose of this handbook is to assist health sector administrators and professionals whose mission is the management, design, construction, and inspection of new hospitals, laboratories, and blood banks with a view to protecting the operation of these facilities and the investment made in them. With this in mind, the new characteristics of the project development stages will be described in the pages that follow, and the procedures for selecting the performance objective will be specified.  We will also discuss how to assess the various siting, design, and construction options, as well as how to select the professional teams that will be involved in the project. While this handbook is not a design or building code, relevant basic concepts will be presented, and reference will be made to specific documents where one can find the appropriate technical recommendations needed to meet the performance objective desired.

In drafting this handbook, only some natural hazards have been taken into account: seismic events, hurricanes and strong winds, landslides, floods, and volcanic eruptions.  Other phenomena—such as drought, fire, or man-made hazards—have been excluded, either because they are unlikely to damage the facility’s operation or investment, or because they are adequately covered elsewhere.

It is also important to acknowledge that different natural phenomena present different challenges to the development of the project. In the case of floods or volcanic activity, generally the only technically and financially feasible option is to select a site that offers the desired level of safety. If landslides, mudslides, or floods are the prevailing hazards, it is often possible to modify the variables that control the phenomenon—for instance, by engaging in extensive tree planting, or building ditches and other water-diversion structures. When it comes to seismic events, hurricanes and strong winds, it is necessary, in addition to correctly choosing the site, to design the structures so that they are resistant to such phenomena. In the specific case of earthquakes, it is necessary to provide safety to the entire infrastructure, both internal and external. In the case of strong winds, protection efforts focus mainly on exposed external components. In extreme situations, the only solution is to distribute the risk by building not one facility but several, distributed spatially, that can perform the desired healthcare functions. Being located in different sites should improve the odds of effective protection, since even if some of them are affected, functional damage will not be total. Being aware of these differences and options should facilitate appropriate and cost-effective risk management.

- Definition of basic concepts

Below, concepts of a general nature are defined to assist the reader.  Definitions of more specific concepts will be presented further on, as part of the relevant chapters.

| Natural hazard | An event of natural origin and sufficient intensity to cause damage in a particular place at a particular time. |
| --- | --- |
| As-built Report | Set of documents concerning project managers, contractual documents, the professionals involved in regional and local risk assessments, the design of the project, construction and inspection procedures, applicable codes and standards, certificates of component safety, final plans for the structure, its components and protection systems, and certificates of compliance with project specifications. |
| Structural components | Elements that are part of the resistant system of the structure, such as columns, beams, walls, foundations, and slabs. |
| Non-structural components | Elements that are not part of the resistant system of the structure. They include architectural elements and the equipment and systems needed for operating the facility. Among the most important non-structural components: architectural elements such as façades, interior partitions, roofing structures, and appendages. Non-structural systems and components include lifelines; industrial, medical and laboratory equipment; furnishings; electrical distribution systems; HVAC systems; and vertical transport systems |
| Structural detailing | A set of measures, based on the theoretical, empirical and experimental experience of the various participating disciplines, for protecting and improving the structural component performance. |
| Non-structural detailing | A set of measures, based on the theoretical, empirical and experimental experience of the various disciplines, aimed at protecting and improving the non-structural component performance. |
| Tender documents | Legal documents that stipulate the characteristics of the design or building contract or contracts (parties involved, financial amounts, deadlines, forms of payment, etc.) and the technical characteristics of the construction (general and detail plans, structural and non-structural components, standards and codes that must be followed, specialized inspection requirements, recommended and unacceptable construction methods, etc.). |
| Specialized inspection | Activities aimed at ensuring that the requirements of the project are met in matters such as quality of the work, the use of construction processes and materials of a quality commensurate with the goals of the project, the fulfillment of the provisions established in the standards and codes referenced in the contracts, and the procurement of component safety certificates and others. |
| Quality assurance | A set of actions aimed at ensuring that project performance objectives are met. |
| # Risk | Extent of the likely losses in the event of a natural disaster. The level of risk is intimately associated with the level of protection incorporated into the structure. |
| Critical services | Services that are life saving, involve hazardous or harmful equipment or materials, or whose failure may generate chaos and confusion among patients or the staff. |
| Resistant system | A structural system especially designed to withstand the impact of natural phenomena. The structural system must be designed in such a way that its detailing is proportional to the performance objective chosen for the structure. |
| Protection systems | Devices and procedures aimed at providing safety to the structural and non-structural components of the building and meeting the performance objective. |
| Vulnerability | The likelihood of a facility that enjoys a particular level of protection suffering material damage or being affected in its operations when exposed to a natural hazard. |

Adapted from Noji, E., Impact of Disasters on Public Health, Pan American Health Organization (PAHO), 2000.

ECLAC/IDB, A Matter of Development: How to Reduce Vulnerability in the Face of Natural Disasters, prepared for the “Confronting Natural disasters: A Matter of Development” Seminar, by Ricardo Zapata M. and Rómulo Caballeros, 2000.

World Health Organization (WHO), Public Health in the Americas: New Concepts, Performance Analysis and Bases for Action, Scientific and Technical Publication Nº 589, 2002.