Chapter IV

Design and Construction of the Project

- Introduction

After selecting the correct site for the facility, it is time to design a project that provides a level of safety commensurate with the performance objective chosen. The protection systems to be used for this purpose must meet two requirements: it must be feasible to build them, and it must not be difficult to provide them with an effective level of maintenance. A poor design will lead to constraints during the other stages of the project that could make it difficult, even impossible, to meet the performance objective.

The acceptable level of damage to the structural and non-structural components of the facility is directly related to the time—and expense—needed for recovery, as defined by the Institution for the various hazards and levels of risk. Table 14 shows the acceptable levels of damage to the facility’s components in terms of the recovery time for different degrees of risk. While recovery times cannot be guaranteed in advance, the matter must be addressed effectively, since it corresponds to the Institution’s very real need to predict when it will be able to start providing its services again during an emergency.

| Table 14 Acceptable Levels of Damage to Components1 |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Intensity of the Hazard |  | Acceptable Level of Damage |  |
| Recovery time | Credible Maximum Desired | Minimum Recommended | Structural Components | Non-structural Components |
| Immediate (Hours) |  |  | Minor | Minor |
| Short (Weeks) |  |  | Minor to Moderate | Minor to Moderate |
| Moderate (Months) |  |  | Moderate | Moderate |
| Long (More than one Year) |  |  | Moderate to Severe | Severe |
| Very Long (Or Never) |  |  | Severe | Not Considered |

| Notes : | 1 | Annex B contains a series of tables, adapted from FEMA 356, listing accepted levels of damage to structural and non-structural components in the event of a “design” earthquake (one two-thirds of the intensity of the maximum considered earthquake, or MCE), based on two different performance objectives for the structural system. |
| --- | --- | --- |

The design process involves seven clearly differentiated stages:

- Drafting of a Medical Architectural Program.

- Selection of the Preliminary plan Development Team.

- Drafting of the Preliminary plan.

- Selection of the Project Development Team.

- Development of the Project.

- Selection of the General Contractor.

- Construction.

In order to implement these stages, it is vital for the Client Institution, which sets the goals and requirements, to act rigorously in the selection of two main teams:

- The Execution Team, which carries out the various tasks required at each stage.

- The Reviewing Team, whose job is quality assurance in compliance with the project goals and needs of the Client Institution.

Chapter V describes the various types of professionals that need to be involved in the project, and the criteria they must meet. As part of the quality assurance strategy, it is necessary to underscore the role played by the Reviewing Team in ensuring that the performance objective is actually met. The Team must establish up coordination mechanisms that can effectively evaluate the implementation of the project and the incorporation of the agreed-upon protection measures. At each stage of the design process, and for each service to be provided, the Team must evaluate whether the performance objective has been achieved.

- Stages in the design and construction of the facility

2.1.	Stage 1: Preliminary Plan

The design process has, as its starting point, a Medical Architectural Program, defined by the Institution, which stipulates the services the new facility will provide and the physical space it will require to do so. The Program typically specifies all the services to be provided, the functional areas needed, and the desired dimensions in square meters. It is on the basis of this Program that the Preliminary Plan will be drafted, and which will define how the services and spaces will be handled. This process must include the definition of the physical characteristics of the facility and its operation.

Taking into consideration the hazards the facility may face, it will be necessary to choose protection methods and systems that can meet the challenges posed by these hazards. For instance, in areas of high seismicity, buildings must be regular in their geometric plan and elevation, and systems that do not lead to sharp deviations in the structural system must be selected. In addition, it is desirable at this stage to establish whether there will be constraints on the form and distribution of the facility as a result of the structure’s protection systems. For instance, if a seismic base isolation system is used, a discontinuity at the isolation interface will be required not only throughout the entire floor plan but also in the immediate perimeter areas, in order to accommodate any displacements that may occur. This situation compels the use of special designs that must be considered at this stage. Likewise, in high-wind areas, the type of roof covering and façade elements is highly relevant. In flood-prone areas, meanwhile, it may be necessary to employ fills above the level of reference that would normally not be considered.

Usually, more than one preliminary plan will be produced for each facility. The selection of the definitive plan, in addition to any functional and aesthetic considerations that may influence the final choice, should be guided by how thoroughly the existing regional and local risks have been taken into account, along with the necessary solutions to secure the performance objective set for the project. Table 15 should be of help in assessing any preliminary plan in terms of the performance objective set for the facility.

Table 15 Preliminary Plan Selection

Prevalent Hazards:

Ways in which those hazards may affect the facility

Ways in which the preliminary plan takes the effects of the various hazards into account

Location

Shape

Structural system, and level and type of protection

Dependence on external services and agencies

Special protection elements contemplated

Particular design considerations

Measures to ensure that the performance objective will be met

Since it is during the Preliminary Plan stage that the requirements of the Medical Architectural Program will be interpreted, and formal solutions found for the protection challenges it poses, it is essential that the Execution Team have enough experience to perform this correctly.

2.2.	Stage 2: Selection of the Design Team

This is the time to define the requirements that must be met by the specialists who will develop the definitive project, and to select the various work groups.

2.3.	Stage 3: Design

The first step in this stage is to to carry out the detailed studies needed for the production of the definitive project, which will consist of technical specifications, plans, mockups, and tender documents (see Flow Chart 5).

Due to the additional complexity of any health facility in comparison with ordinary bldgs without the same stringest occupancy requirements, a large number of professionals (grouped by discipline as specified in Table 24) must participate. Each team of specialists will be in charge of developing a specific subproject: the structure, the heating, ventilation and air conditioning (HVAC) system, the various support services, and so on. Coordination is required for all these activities, and therefore clear procedures and protocols must be defined for the generation and sharing of information. Appropriate coordination is the key to the successful completion of this stage.

From the point of view of vulnerability reduction and the fulfillment of the performance objective, the Design Coordination Team must advise each of the specialized work groups on the functional and protection requirements specified for the facility and its services. Each team of specialists will be called on to prepare a document in which it clearly explains how it will achieve these objectives and, most importantly, what their requirements and restrictions will be in relation to the other disciplines in order to meet these objectives.

The design of the project will be the result of the integration of the work of all the participating disciplines on each section of the contemplated facility, so it bears repeating that coordination is indispensable. The safety criteria chosen for each section has to be the same across all disciplines, and the ways in which they will be met must be established in advance by all teams. The protection systems that will be incorporated must then be included in the construction documents outlining the physical details of the system to be built: the technical specifications and the various plans.

#### Flow Chart 5

Design of the Project

DESIGN SELECTION OF DISCIPLINES/DESIGN GROUPS WORK BY TEAM OF SPECIALISTS 1 PROJECT: PLANS SPECIFICATIONS MOCKUPS BUDGET TENDER DETAILS OTHER DOCUMENTS VERIFICATION OF THE FULFILLMENT OF THE PERFORMANCE OBJECTIVE TENDER DEFINITION OF WORK PLANS AND QUALITY ASSURANCE ADEQUATE INADEQUATE QUALITY ASSURANCE VULNERABILITY CONTROL ASSURANCE WORK BY TEAM OF SPECIALISTS 2 WORK TEAM OF SPECIALISTS 3

When considering the overall safety of the infrastructure in question, it is common to classify its components into two groups: the structure itself, and the non-structural elements. Generally, the design team in charge of the structure is proficient in two disciplines: structural engineering and architecture. In the design of the non-structural elements, all disciplines must be equally involved.

2.3.1.	Design of the structure

      - Characteristics of the structural design

The structural system must meet the performance objectives defined for the facility as a whole and the services it will provide. The structural engineering team is chiefly responsible for the safety of the structure. When the performance objectives of the facility and its services call for investment and functional protection, the team must provide a structural system that not only safeguards the structure itself but also the non-structural elements. Put differently, the structure not only must protect—it must make it feasible to implement procedures for protecting the non-structural systems. For this reason, the structural system needs to be approved by all the disciplines represented in the project.

At present, non-traditional structural systems provide different levels of safety both for the structure and the non-structural elements. For instance, in the case of seismic demand, several hospitals have been built successfully employing seismic base isolation systems, which create an interface between the foundations and the structure through the use of rubber or friction-pendulum bearings that simulate a car’s suspension system. Such systems keep the seismic energy from reaching the structure through dissipation, reducing significantly the impact of strong ground motion on the structure and non-structural elements.

The structural system and its components must be designed to withstand the permanent and potential forces that affect a structure, including its dead load (its own weight) as well as its live load (the structure in operation), its seismic load, wind load, snow or ash load, temperature changes, hydrostatic and hydrodynamic soil factors, total and relative settlements of foundations, and so on, all of which are defined and regulated by existing design standards.

In general terms, the design must incorporate structural detailing that can effectively meet the protection objective for each level of risk. It is also important to incorporate in the design any systems that, in case of damage and functional losses, may enable the facility’s services to recover within a predefined timeframe.

Given the materials that are employed in construction, there will always be some degree of damage. For instance, damage to reinforced concrete buildings may present itself as fissures, cracking, or the partial or total collapse of the material. However, no level of damage is acceptable if it put the lives of the users or staff at risk. To the fullest extent possible, moreover, situations must be prevented that can cause panic among the staff and the evacuation of the facility when it is technically unnecessary.

The following form summarizes the aspects that must be evaluated by the Design Coordination Team in order to verify that a level of safety adequate to the design of the structural system has been incorporated.

Form 4

      - Information provided by the Structural Design Team

The Structural Design Team must request, and later provide, the information required by the other disciplines for the design of the equipment, systems, and other non-structural components. Table 16 illustrates some of the data that must be exchanged.

Table 16 Information that must be provided by the Structural Design Team

Story drift ratio

Forces acting on the points of support

Acceleration at each story

Others (Specify)

The Project Coordination Team must ensure that this information is taken into account by all the other disciplines working on the design of the project.

      - Safety assessment of the structural system

The specialists in charge of the structural design of the facility must be able to guarantee that the protection criteria set by the institution will be met. The following forms, included for illustrative purposes only, list the minimum background data that must be assessed by each of the specialist teams if seismic or high-wind hazards are present at the facility’s intended site.

Form 5

Form 6

2.3.2.	The design of non-structural components

2.3.2.1	Characteristics of the design of non-structural components

Non-structural elements are those components that, while not being part of the resistant system of the structure, are crucial to the effective operation of the facility. In the case of hospitals, close to 80 percent of the total bill for the facility goes into non-structural components, among them architectural elements, medical and laboratory equipment, office equipment, electrical and mechanical-industrial equipment, distributed lines, and basic installations.

The impact of damage to the facility’s non-structural components may vary. For instance, damage to medical equipment or to the lifelines that supply medical and support services can actually cause loss of lives or—what often amounts to the same thing—the loss of the functional capacity of the facility. While less dramatic, partial or total damage to certain components, equipment, or systems may entail prohibitive repair and replacement costs. Major damage to systems, components, or equipment containing or involving harmful or hazardous materials may force the evacuation of some parts of the facility, resulting in a loss of operational capacity.

Secondary effects of the damage to non-structural components are also important, for instance the fall of debris in hallways or escape routes, fires or explosions, or the rupture of water or sewerage pipes. Even relatively minor damage, it should be stressed, can compromise aseptic conditions in the affected areas, putting critical patients at risk.

Non-structural components must incorporate a level of protection that is proportional to the performance objective that has been defined for the medical or support service in question, as well as all other services that are directly or indirectly related to them. Each team of specialists must be responsible for the design of the protection systems required by the components of their competence, and must certify, by following the procedures described in section 2.3.2.2, that the performance objective defined by the institution has been met.

The Project Coordination Team must ensure that the subprojects designed by the various disciplines are correctly integrated and compatible with each other, and it should hold regular coordination meetings in which representatives of each team are present. Moreover, the Coordination Team will be responsible for ensuring that each work group is provided in timely fashion with the most up-to-date information regarding the work of the other teams and the overall progress of the project.

Table 17 and Form 7 should assist the Project Coordination Team in verifying that protection systems are being effectively incorporated in the various non-structural components that typically require protection.

| Table 17 Typical Non-structural Components that Require Protection |  |  |
| --- | --- | --- |
| Architectural | Equipment and Furnishings | Basic facilities |
| Partitions | Medical equipment | Medical gases |
| Interiors | Industrial equipment | Industrial gas |
| Façades | Office equipment | Electric distribution |
| Suspended ceilings | Furniture | Telecommunications |
| Roofs or decks | Contents | Vacuum |
| Cornices | Supplies | Drinking water |
| Terraces | Clinical files | Industrial water |
| Chimneys | Pharmacy shelves | Air conditioning |
| Plaster |  | Steam |
| Glass windows |  | Piping in general |
| Appendages |  |  |
| Canopies |  |  |
| Antennas |  |  |

| Source: | Boroschek, R. and Astroza, M. Disaster mitigation in Health facilities: Non-structural Aspects, Pan American Health Organization, 2000. |
| --- | --- |

The protection of non-structural systems calls for a logical sequence: first, interior safety and the stipulation of requirements for the immediate exterior (characteristics of supports, anchoring, etc.); secondly, the safety of the immediate exterior (furnishings, ceilings, supplies and others); and, finally, the safety of the overall structure. The following table summarizes the main ways to protect non-structural components:

| Table 18 Main Forms of Protection |  |  |  |
| --- | --- | --- | --- |
| Non-structural Component to Protect | Protection Provided by: |  |  |
|  | Structure | Architecture | Furnishings |
| Architectural |  |  |  |
| Industrial equipment |  |  |  |
| Medical and laboratory equipment |  |  |  |
| Distributed systems |  |  |  |

Form 7

2.3.2.2	Assessing the safety of non-structural components

Non-structural components require protection systems that can guarantee the achievement of the performance objective set for the project. Assessing the degree to which the protection goals for the different disaster scenarios have been met may be done in several ways, most commonly through mathematical modeling or certificates issued by the supplier or manufacturer of the component or system.

Tables 19a and 19b summarize the procedures that each discipline must follow in order to assess potential protection systems.

#### Table 19a #### Safety Assessment of Systems, Equipment and Non-structural Components through Mathematical Analysis1

Minimum required content of Calculation Log2

Identity of the specialist

Name of the specialist

Discipline

Classification of the system, equipment or component

Architectural element

Lifeline

Medical or laboratory equipment

Industrial equipment

Isolated electrical or mechanical equipment

Distributed electrical or mechanical equipment

Level of protection under consideration

# Performance objective for the overall facility and the area where the system, equipment or component is located

Performance objective for the services supported by the system, equipment or component

Performance objective for the system, equipment or component itself

Standards considered in the analysis

National standards

International standards

Other standards specific to the project

Description of the structure where the system, equipment or component will be located

Geometrical dimensions

Number of stories

Height of stories

Estimated load of the various stories of the building

Essential facts on the dynamic properties of the building

Other essential facts

Behavior determining the response of the system, equipment or component

Interior safety

Support element or anchoring

Anchoring

Bracing

Stability (overturning, sliding)

Deformation

Resistance

Highest level of damage tolerated

Interaction with other elements

Dependence on other elements

Other (specify)

Description of the system, equipment or component

General description, function, and dependence on other systems, equipment or components

Weight, distribution of the weight, and location of the center of mass in different conditions of use and operation

Geometrical dimensions

Chief materials and mechanical characteristics

Support systems

With vibration isolation system

Without vibration isolation system

Detail plans or sketches

Interior safety certificate issued by the supplier or manufacturer

Background facts on performance in previous emergencies

Description of built-in protection systems

Systems used for the interior safety of the component

Systems used to increase the safety to the support element

Systems used for anchoring and stabilization

Systems used for damage control

Systems used to prevent interaction with other components

Other systems used to provide safety to the system, equipment or component

Characteristics of the equipment when in operation (Evaluate only relevant equipment)

Frequency of operation

Storage capacity

Loads produced during the operation of the equipment

Operational temperature

Operation in corrosive environment

Identity of least favorable actions and load combinations 3

Bracing characteristics of systems, equipment and components

Description of the structural concept

Degree of Inclination of the braces

Length of the braces

Profile section of braces

Thickness of the bracing element

Capacity of the material

Elasticity of the material

Distance between braces

Detail plans

Anchorage characteristics of systems, equipment and components

Description of the structural concept

Resistance of the materials

Number of anchoring elements

Diameter of the anchoring elements

Embedded length of the anchoring elements

Plans of the anchoring elements

Characteristics of system, equipment or component support elements

Material

Shape of the elements

Resistance of the materials

Other characteristics of the support elements

Classification of the system, equipment or component

Fundamental period To

Rigid equipment or component

High deformability

Limited deformability

Low deformability

Flexible equipment or component

High deformability

Limited deformability

Low deformability

Spatial distribution

Isolated element

Distributed element

Number of points of support

Response

Sensitive to acceleration

Sensitive to deformation

Contents

Hazardous or difficult-to-replace materials

Materials not dangerous nor difficult to replace

Interaction with other systems, equipment and components

Not linked

Linked

Dependence on other systems, equipment and components

Independent

Dependent

Other relevant classifications

Method of analysis

Equipment included in structure analysis model

Equipment not included in structure analysis model

Static analysis

Dynamic analysis

Characteristics of the demand

Summary of factors that determine the demand

Return period associated with the expected demand

Damping considered

Factors that may modify the response

Demand as it is considered in the design

Results

Internal efforts

Utilization factors of bracing elements

Utilization factors of anchoring elements

Estimated deformation

Assessment of the system, equipment or component’s bracing or anchoring elements

Stability

Assessment of interaction with other systems, equipment or components

Assessment of potential impacts

Assessment of potential contamination by hazardous or harmful materials

Confirmation that Objectives have been met

| Notes: | 1 | The table above applies to architectural elements, industrial equipment, medical and laboratory equipment, lifelines and other components of the services that need to be protected. In the case of each item, the data regarding the equipment or component analyzed should be evaluated individually. |
| --- | --- | --- |
|  | 2 | The calculation log should include all computational processes and the results of the intermediate calculations. |
|  | 3 | In addition to the load caused by the potential emergency--the dead load, the live load, the load caused by the failure of the equipment, the load associated with electrical or mechanical failure, the load derived from the interaction with other equipment or components, and the load stipulated in the contract standards. |

#### Table 19b #### Standardized Safety Assessment of Systems, Equipment and Non-structural Components through Certification by the Supplier or Manufacturer1

Analysis-based Certification

A calculation log must be attached covering the contents specified in 19a, in accordance with the level of detail required by the study. This document will be used for reviewing the safety of the component

Experimental Certification

Identity of accredited laboratory

Standards of reference employed in the tests

Description of test procedures

Demand applied in the tests

Results of the tests

Certification Requirements

Conditions of use and operation

Conditions of installation

Other conditions

Date of certification and validity of the certification

Certification of compliance with standards specified in the contract

Description of limitations and applicability of the certification

| Notes: | 1 | The previous table applies to architectural elements, industrial equipment, medical and laboratory equipment, lifelines and other standard components related to the services that will be protected. |
| --- | --- | --- |

2.3.2.3	Safety assessment of non-structural components

The various teams of specialists must guarantee that the performance objective set for the project has been met. The following form, included for illustrative purposes only, lists the minimum background data that must be taken into consideration by each of the disciplines:

Form 8

The design stage concludes with the production of the final plans, technical specifications, mockups, budgets of reference, and tender documents. At this stage, both the Design Execution Team and the Project Reviewing Team must deliver a document certifying that the Protection Objective has been met.

2.4.	Stage 4: Selection of the General Contractor

The selection of the General Contractor who will engage in the actual construction of the facility must meet all relevant national legislation and standards. Among the selection criteria, the experience of candidate firms in the building of disaster-resistant health facilities should be considered. Chapter V describes the requirements that must be met by the companies interested in bidding for the contract.

2.5.	Stage 5: Construction

It is at this stage that the performance objective set for the facility must be realized. Quality assurance Procedures such as those mentioned in Chapter VI must now be rigorously followed in order to ensure that protection goals are met.

While the project’s specifications and plans should guide the construction process, in practice it is often necessary to introduce modifications or clarify the meaning of certain requirements. In such situations, any request for modifications presented by the Contractor must be meticulously evaluated, and any alteration to the original plans should be approved by the Client Institution, the Design Team, and the Reviewing Team. Modifications to the facility’s performance objective must be subjected to careful analysis and discussion, which needs to be documented—thereby ensuring that the facility’s real operational capacity within the overall health network has been correctly determined.

- References

  - Standards, codes and general protection reference material

American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures.

Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000.

Building Officials Code Administrators International, International Building Code 2000.

Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001.

Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986.

Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988.

Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981.

European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998.

Federal Emergency Management Agency, FEMA 276: Example Applications of the NEHRP Guidelines for the Seismic Rehabilitation of Buildings, Washington, D.C., April 1999.

Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Assessment of Existing Buildings, Washington, D.C., 1998.

Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000.

Federal Emergency Management Agency, FEMA 55: Coastal Construction Manual.

Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, TO Practical Guide, Washington, D.C., September 1994.

International Standards Organization, ISO 3010:2001: Basis for Design of Structures—Seismic Actions on Structures.

International Standards Organization, ISO 4354:1997: Wind Actions on Structures.

Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001.

U.S. Army Corps of Engineers, Engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998.

  - Standards, codes and references specific to protection of structural components and non-structural.

Tables 20 and 21 show examples of specific standards, codes and references that may be considered in the design of the protection systems of the structural and non-structural components.

| Table 20 Protection of Structural Components |  |
| --- | --- |
| Natural hazard | Standards, Codes and References Specific to Design and Analysis |
| Strong winds | American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures. Building Officials Code Administrators International, International Building Code 2000. Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981. European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998. Federal Emergency Management Agency, FEMA 55: Coastal Construction Manual. Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994. International Standards Organization, ISO 4354:1997: Wind Actions on Structures. |
| Seismic event | American Society of Civil Engineers, ASCE 7-98: Minimum Design Loads for Buildings and Other Structures. Applied Technology Council, ATC 51: U.S.-Italy Collaborative Recommendations for Improving the Seismic Safety of Hospitals in Italy, California, 2000. Building Seismic Safety Council (BSSC), FEMA 368: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Washington, D.C., 2001. Building Seismic Safety Council (BSSC), FEMA 369: NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures, Commentary, Washington, D.C., 2001. Building Officials Code Administrators International, International Building Code 2000. Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.1: Seismic Design Guidelines for Essential Buildings, Technical Manual, Washington, D.C., December 1986. Departments of the Army, the Navy and the Air Force, NAVY NAVFAC P-355.2: Seismic Design Guidelines for Upgrading Existing Buildings, Technical Manual, Washington, D.C., September 1988. Deutsches Institut für Normung, DIN 4149-1: Buildings in German Earthquake Zones; Design Loads, Dimensioning, Design and Construction of Conventional Buildings, 1981. European Committee for Standardization, Eurocode 8: Design of Structures for Earthquake Resistance. Part 1: General Rules, Seismic Actions and Rules for Buildings, Brussels, 1998. Federal Emergency Management Agency, FEMA 74: Reducing the Risk of Nonstructural Earthquake Damage, A Practical Guide, Washington, D.C., September 1994. Federal Emergency Management Agency, FEMA 276: Example Applications of the NEHRP Guidelines for the Seismic Rehabilitation of Buildings, Washington, D.C., April 1999. Federal Emergency Management Agency, FEMA 310: Handbook for the Seismic Assessment of Existing Buildings, Washington, D.C., 1998. Federal Emergency Management Agency, FEMA 356: Prestandard and Commentary for the Seismic Rehabilitation of Buildings, Washington, D.C., November 2000. International Standards Organization, ISO 3010:2001: Basis for Design of Structures—Seismic Actions on Structures. Office of Statewide Health Planning and Development (OSHPD), Building Standard Administrative Code, Part 1, Title 24, C.C.R, December 2001. U.S. Army Corps of Engineers, engineering Division, Directorate of Military Programs, TI 809-4: Seismic Design for Buildings, Technical Instructions, Washington, D.C., December 1998. |

| Table 21 Protection of Non-structural Components |  |  |
| --- | --- | --- |
| Non-structural Component | Standards, Codes and References Specific to Design and Analysis | Professional Team Required |
| Isolated (not distributed) electrical and mechanical equipment Industrial equipment | American Petroleum Institute, API 650: Welded Steel Tanks for Oil Storage, Washington, D.C. Deutsches Institut für Normung, DIN IN 61587-2: Mechanical Structures for Electronic Equipment - Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks (IEC 61587-2:2000), 2001. Ishiyama, Y., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. Institute of Electrical and Electronic Engineers, IEEE C 37.81: Guide for Seismic Qualification of Class 1E Metal-Enclosed Power Switchgear Assemblies, New York, 1989. Institute of Electrical and Electronic Engineers, IEEE C 37.98: Seismic Testing of Relays, New York, 1987. Institute of Electrical and Electronic Engineers, IEEE 344-1987: Recommended Practice for Seismic Qualification of Class 1E Equipment for Nuclear Power Generating Stations, New York, 1987. International Electrotechnical Commission, IEC 60068-3-3: Environmental Testing – Part 3, Seismic Test Methods for Equipment, 1991. International Electrotechnical Commission, IEC 60255-21-3: Electrical relays - Part 21: Vibration, Shock, Bump and Seismic Tests on Measuring Relays and Protection Equipment - Section 3: Seismic Tests, 1988. International Electrotechnical Commission, IEC 61166-21-2: High-Voltage Alternating Current Circuit-Breakers - Guide for Seismic Qualification of High-Voltage Alternating Current Circuit-Breakers, 1993. International Electrotechnical Commission, IEC 62271-002: Amendment 1 to IEC 61166: Gas-Insulated Metal-Enclosed Switchgear for Rated Voltages of 72.5 kV and Above - Guide for Seismic Qualification. International Electrotechnical Commission, IEC/TS 61463: Bushings - Seismic Qualification, 2000. International Electrotechnical Commission, IEC 61587-2: Mechanical Structures for Electronic Equipment – Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks. Ishiyama, Y.., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. | Electrical engineer Mechanical engineer Seismic engineer Structural engineer Vulnerability assessment specialist Hospital architect Industrial equipment specialist |
| Pipes, ducts and electrical conduit systems Fire safety systems | National Fire Protection Association, NFPA 13: Standard for the Installation of Sprinklers Systems. Sheet Metal and Air Conditioning Contractors National Association, Seismic Restraint Manual: Guidelines for Mechanical Systems & Addendum Nº1. WSP 029, Aseismic Design Manual for Underground Steel Water Pipelines, 1989. | Electrical engineer Mechanical engineer Seismic engineer Structural engineer Vulnerability assessment specialist Fire Protection Specialist |
| Medical and laboratory equipment Furniture | International Electrotechnical Commission, IEC 60068-3-3: Environmental Testing - Part 3: Guidance. Seismic Test Methods for Equipment, 1991. Ishiyama, Y., Criteria for Overturning of Rigid Bodies by Sinusoidal and Earthquake Excitations, Earthquake Engineering and Structural Dynamics, Vol. 10, 1981. | Hospital architect Medical equipment specialist Seismic engineer Structural engineer Vulnerability assessment specialist Furniture designer |
| Systems of Suspended ceilings Lighting fixtures Systems | American Society for Testing and Materials, ASTM E 580: Standard Practice for Application of Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels in Areas Requiring Moderate Seismic Restraint, 2000. Ceilings and Interior Systems Construction Association, Guidelines for Seismic Restraint, Direct Hung Suspended Ceilings Assemblies: Seismic Zones 3-4, 1991. Uniform Building Code Standard 25-2: Metal Suspension Systems for Acoustical Tile and for Lay-in Panel Ceiling. | Hospital architect Specialist lighting fixtures Seismic engineer Structural engineer Vulnerability assessment specialist |
| Vertical transport systems | American Society of Mechanical Engineers, ASME A17.1: Safety Code for Elevators and Escalators, 1996. Deutsches Institut für Normung, DIN IN 61587-2: Mechanical Structures for Electronic Equipment - Tests for IEC 60917 and IEC 60297 - Part 2: Seismic Tests for Cabinets and Racks (IEC 61587-2:2000), 2001. Japanese Elevator Association, Guide for Earthquake Resistant Design and Construction of Vertical Transportation. Standard New Zealand, NZS 4332:1997: Non Domestic Passenger and Goods Lifts. 1997. | Vertical transport specialist Mechanical engineer Electrical engineer Seismic engineer Structural engineer Vulnerability assessment specialist |
| Roofing structures | Federal Emergency Management Agency, Against the Wind. | Hospital architect Seismic engineer Structural engineer Vulnerability assessment specialist |
| Partitions and façade elements | American Architectural Manufacturers Association, Aluminum Curtain Wall Design Guide Manual American Architectural Manufacturers Association, Aluminum Store Front and Entrance Manual American Architectural Manufacturers Association, Design Windloads for Buildings and Boundary Layer Wind Tunnel Testing American Architectural Manufacturers Association, Installation of Aluminum Curtain Walls American Architectural Manufacturers Association, Maximum Allowable Deflection of Framing Systems for Building Cladding Components at Design Wind Loads American Architectural Manufacturers Association, Metal Curtain Wall Fasteners American Architectural Manufacturers Association, Metal Curtain Wall Manual American Architectural Manufacturers Association, Rain Penetration Control – Applying Current Knowledge American Architectural Manufacturers Association, Structural Design Guidelines for Aluminum Framed Skylights American Architectural Manufacturers Association, Voluntary Specifications for Hurricane Impact and Cycle Testing of Fenestration Products. Federal Emergency Management Agency, Against the Wind. | Hospital architect Seismic engineer Structural engineer Vulnerability assessment specialist |
| Doors and windows | American Architectural Manufacturers Association, Glass and Glazing. Federal Emergency Management Agency, Against the Wind. International Standards Organization, ISO 6612:1980: Windows and Door Height Windows Wind Resistance Tests. | Hospital architect Structural engineer |

Principles of Natural Disaster Mitigation in Health Facilities (Pan American Health Organization, 2000), Disaster Mitigation for Health Facilities: Guidelines for Vulnerability Appraisal and Reduction in the Caribbean (PAHO, 2000), and FEMA 55: Coastal Construction Manual (Federal Emergency Management Agency, 1996) list the basic requirements for each hazard.